## Summary
Hydraulic analysis - Tunduma Water Supply Project - Momba (Saisi) River to Tunduma, design year 2035
HYDRAULIC ANALYSIS - Tunduma Water Supply Project - Momba (Saisi) River to Tunduma, design year 2035
Friction: hazen-williams, minor losses 10% of friction where no K given, water 20.0 degC
Min pressure 5.0 m at junctions, 2.0 m along mains (pipe crown 1.2 m below ground), station losses 3.0 m, surge factor 1.0 x Joukowsky, PN check EN 805 (PMA = 1.2 x PFA)
Raw water abstraction: 21,505 m3/day Water delivered to demand nodes: 20,000 m3/day
PIPES
Pipe From -> To DN L (m) h/d Q (m3/d) Q (l/s) V (m/s) Loss (m) m/km HGL in HGL out Pmin Pmax Surge PN
----------------- --------------------------- --- ------ --- -------- ------- ------- -------- ----- ------- ------- ---- ----- ----- ----
ABSTRACTION MOMBA_RIVER -> MOMBA_INTAKE 600 100 22 21,505 272 0.96 0.2 1.78 1,361.0 1,360.8 - 2.0 98 PN10
LL_DELIVERY MOMBA_INTAKE -> GRIT_TANK 600 30 22 21,505 272 0.96 0.1 1.78 1,369.1 1,369.0 - 4.3 98 PN10
RAW_MAIN GRIT_TANK -> MOMBA_WTP 600 1,078 22 21,505 272 0.96 1.9 1.78 1,380.9 1,379.0 8.3 16.2 98 PN10
WTP_IKANA_RM MOMBA_WTP -> IKANA_GBR 600 19,666 22 20,000 253 0.89 30.6 1.56 1,699.6 1,669.0 8.9 328.6 91 PN40
IKANA_NKANGAMO_GM IKANA_GBR -> NKANGAMO_BPS 600 38,930 24 20,000 231 0.82 51.6 1.33 1,663.3 1,611.7 65.6 205.9 83 PN25
BPS_RM_1 NKANGAMO_BPS -> J-001N 600 19,581 22 20,000 253 0.89 30.5 1.56 1,738.2 1,707.7 6.7 183.9 91 PN25
BPS_RM_2 J-001N -> J-002N 600 40 22 19,628 248 0.88 0.1 1.50 1,707.7 1,707.7 9.6 10.6 89 PN10
BPS_RM_3 J-002N -> J-003N 600 100 22 18,082 228 0.81 0.1 1.29 1,707.7 1,707.5 9.2 9.6 82 PN10
UHURU_INLET J-003N -> UHURU_PARK_GBR 600 50 22 17,460 220 0.78 0.1 1.21 1,707.5 1,707.5 9.4 11.4 79 PN10
ESR_BRANCH J-001N -> TUNDUMA_ESR 100 38 22 372 5 0.60 0.2 5.98 1,707.7 1,707.5 10.6 10.6 61 PN10
GSR01_BRANCH J-002N -> UHURU_GSR01 150 40 22 1,547 20 1.11 0.5 11.64 1,707.7 1,707.2 9.6 10.0 113 PN10
IPITO_BRANCH J-003N -> IPITO_GSR02 150 4,221 22 622 8 0.44 9.1 2.16 1,707.5 1,698.4 9.0 97.9 45 PN16
UHURU_J004N UHURU_PARK_GBR -> J-004N 150 1,563 24 1,244 14 0.81 10.4 6.62 1,697.6 1,687.2 -1.9 58.4 83 PN10
MAKAMBINI_BRANCH J-004N -> MAKAMBINI_GSR03 100 494 24 622 7 0.92 6.5 13.22 1,687.2 1,680.7 58.4 58.4 93 PN10
CHAPWA_BRANCH J-004N -> CHAPWA_GSR04 100 2,790 24 622 7 0.92 36.9 13.22 1,687.2 1,650.4 58.4 127.8 93 PN25
* = diameter chosen by the program; pressures in m of water; PN column basis: working
PN by chainage along each pipe - working pressure only / including surge:
ABSTRACTION: PN10 (0-100 m)
PN10 (0-100 m) (incl. surge 98 m)
LL_DELIVERY: PN10 (0-30 m)
PN10 (0-30 m) (incl. surge 98 m)
RAW_MAIN: PN10 (0-1,078 m)
PN10 (0-1,078 m) (incl. surge 98 m)
WTP_IKANA_RM: PN40 (0-1,450 m), PN30 (1,450-12,227 m), PN25 (12,227-18,973 m), PN16 (18,973-19,408 m), PN10 (19,408-19,666 m)
PN40 (0-5,926 m), PN30 (5,926-17,427 m), PN25 (17,427-19,408 m), PN10 (19,408-19,666 m) (incl. surge 91 m)
IKANA_NKANGAMO_GM: PN10 (0-170 m), PN16 (170-381 m), PN25 (381-7,257 m), PN16 (7,257-9,906 m), PN25 (9,906-10,006 m), PN16 (10,006-10,706 m), PN25 (10,706-12,707 m), PN16 (12,707-13,307 m), PN25 (13,307-14,358 m), PN16 (14,358-19,259 m), PN10 (19,259-19,659 m), PN16 (19,659-24,061 m), PN25 (24,061-24,611 m), PN16 (24,611-25,611 m), PN25 (25,611-34,667 m), PN16 (34,667-35,217 m), PN25 (35,217-35,367 m), PN16 (35,367-38,930 m)
PN16 (0-170 m), PN25 (170-16,609 m), PN16 (16,609-16,709 m), PN25 (16,709-17,509 m), PN16 (17,509-17,809 m), PN25 (17,809-18,659 m), PN16 (18,659-20,459 m), PN25 (20,459-38,930 m) (incl. surge 83 m)
BPS_RM_1: PN25 (0-613 m), PN16 (613-1,513 m), PN25 (1,513-2,553 m), PN16 (2,553-5,495 m), PN25 (5,495-5,776 m), PN16 (5,776-7,558 m), PN10 (7,558-19,581 m)
PN25 (0-7,518 m), PN16 (7,518-10,116 m), PN10 (10,116-10,756 m), PN16 (10,756-13,483 m), PN10 (13,483-16,224 m), PN16 (16,224-16,504 m), PN10 (16,504-19,581 m) (incl. surge 91 m)
BPS_RM_2: PN10 (0-40 m)
PN10 (0-40 m) (incl. surge 89 m)
BPS_RM_3: PN10 (0-100 m)
PN10 (0-100 m) (incl. surge 82 m)
UHURU_INLET: PN10 (0-50 m)
PN10 (0-50 m) (incl. surge 79 m)
ESR_BRANCH: PN10 (0-38 m)
PN10 (0-38 m) (incl. surge 61 m)
GSR01_BRANCH: PN10 (0-40 m)
PN16 (0-40 m) (incl. surge 113 m)
IPITO_BRANCH: PN10 (0-2,734 m), PN16 (2,734-2,871 m), PN10 (2,871-3,268 m), PN16 (3,268-3,366 m), PN10 (3,366-4,221 m)
PN10 (0-2,384 m), PN16 (2,384-3,793 m), PN10 (3,793-4,221 m) (incl. surge 45 m)
UHURU_J004N: PN10 (0-1,563 m)
PN10 (0-815 m), PN16 (815-1,563 m) (incl. surge 83 m)
MAKAMBINI_BRANCH: PN10 (0-494 m)
PN16 (0-494 m) (incl. surge 93 m)
CHAPWA_BRANCH: PN10 (0-599 m), PN16 (599-2,587 m), PN25 (2,587-2,790 m)
PN16 (0-599 m), PN25 (599-2,790 m) (incl. surge 93 m)
PUMP STATIONS
Station Type Pumps h/d Q/pump m3/h l/s Suction LWL Delivery HGL TDH (m) Shaft kW Motor kW kWh/day kWh/m3 NPSHa
------------ ------ ----- --- ----------- --- ----------- ------------ ------- -------- -------- ------- ------ -----
MOMBA_INTAKE INTAKE 1w+1s 22 978 272 1,360.0 1,369.1 12.1 43 55 1,002 0.05 -
GRIT_TANK SUMP 1w+1s 22 978 272 1,366.5 1,380.9 17.4 62 75 1,448 0.07 -
MOMBA_WTP WTP 3w+1s 22 303 84 1,368.5 1,699.6 334.1 354 450 24,575 1.23 -
NKANGAMO_BPS BPS 2w+1s 22 455 126 1,553.0 1,738.2 188.2 299 355 13,844 0.69 -
MOMBA_INTAKE: head set by inlet of GRIT_TANK (level 1368.0 m + 1.0 m)
GRIT_TANK: head set by inlet of MOMBA_WTP (level 1378.0 m + 1.0 m)
MOMBA_WTP: head set by inlet of IKANA_GBR (level 1668.0 m + 1.0 m)
NKANGAMO_BPS: head set by inlet of TUNDUMA_ESR (level 1706.5 m + 1.0 m)
GRAVITY ZONES
Start Available (m) Required (m) Surplus (m) Status Governed by
-------------- ------------- ------------ ----------- ------------- -------------------------------------------------------------------
MOMBA_RIVER 1,361.0 1,360.2 0.8 OK inlet of MOMBA_INTAKE (level 1360.0 m + 0.0 m)
IKANA_GBR 1,663.3 1,610.1 53.2 OK inlet of NKANGAMO_BPS (level 1557.5 m + 1.0 m)
UHURU_PARK_GBR 1,697.6 1,701.5 -3.9 SHORT OF HEAD pipe UHURU_J004N at 179 m (pipe crown 1698.3 m + 2 m min. pressure)
TANKS
Tank BWL TWL Arrival HGL Excess head Inflow m3/d h/d Required m3 Volume m3 Storage h
--------------- ------- ------- ----------- ----------- ----------- --- ----------- --------- ---------
IKANA_GBR 1,663.3 1,668.0 1,663.3 0.0 20,000 22 1,667 3,000 3.6
UHURU_PARK_GBR 1,697.6 1,702.3 1,697.6 4.2 17,460 22 1,455 5,000 6.9
TUNDUMA_ESR 1,703.5 1,706.5 1,707.5 0.0 372 22 31 120 7.8
UHURU_GSR01 1,698.4 1,701.4 1,707.2 4.8 1,547 22 129 500 7.8
IPITO_GSR02 1,681.2 1,684.2 1,698.4 13.2 622 22 52 200 7.7
MAKAMBINI_GSR03 1,655.7 1,658.7 1,680.7 21.0 622 24 0 200 7.7
CHAPWA_GSR04 1,521.4 1,524.4 1,650.4 125.0 622 24 0 200 7.7
WARNINGS / DESIGN NOTES
[UHURU_PARK_GBR] gravity zone from Uhuru Park GBR 5,000 m3 (Tunduma) is short of head by 3.9 m - increase pipe sizes (or set dn 'auto') or add a booster pump
[RAW_MAIN] pump trip / valve closure can drop pressure to -90 m (surge 98 m) - surge protection needed (surge vessel, air valves)
[WTP_IKANA_RM] pump trip / valve closure can drop pressure to -82 m (surge 91 m) - surge protection needed (surge vessel, air valves)
[IKANA_NKANGAMO_GM] pump trip / valve closure can drop pressure to -18 m (surge 83 m) - surge protection needed (surge vessel, air valves)
[BPS_RM_1] pump trip / valve closure can drop pressure to -84 m (surge 91 m) - surge protection needed (surge vessel, air valves)
[IPITO_BRANCH] pump trip / valve closure can drop pressure to -36 m (surge 45 m) - surge protection needed (surge vessel, air valves)
[UHURU_J004N] negative pressure -1.9 m along the pipe - HGL below ground
[UHURU_J004N] pump trip / valve closure can drop pressure to -85 m (surge 83 m) - surge protection needed (surge vessel, air valves)
[CHAPWA_BRANCH] pump trip / valve closure can drop pressure to -35 m (surge 93 m) - surge protection needed (surge vessel, air valves)
[MAKAMBINI_BRANCH] pump trip / valve closure can drop pressure to -35 m (surge 93 m) - surge protection needed (surge vessel, air valves)
[NKANGAMO_BPS] arrives with 53.2 m excess head - fit a flow control valve / PRV at the inlet or reduce the pipe size
[IPITO_GSR02] arrives with 13.2 m excess head - fit a flow control valve at the inlet
[MAKAMBINI_GSR03] arrives with 21.0 m excess head - fit a flow control valve / PRV at the inlet or reduce the pipe size
[CHAPWA_GSR04] arrives with 125.0 m excess head - fit a flow control valve / PRV at the inlet or reduce the pipe size
COMPARISON WITH THE EMPLOYER'S REQUIREMENTS (schematic Fig. 2)
Link ER L (m) Plan L (m) Model L (m) Diff (m) Q (m3/d) h/d V (m/s)
----------------- -------- ---------- ----------- -------- -------- --- -------
ABSTRACTION 100 - 100 0 21,505 22 0.96
LL_DELIVERY - - 30 - 21,505 22 0.96
RAW_MAIN 1,177 1,078 1,078 -99 21,505 22 0.96
WTP_IKANA_RM 20,994 19,639 19,666 -1,328 20,000 22 0.89
IKANA_NKANGAMO_GM 38,504 38,877 38,930 426 20,000 24 0.82
BPS_RM_1 21,673 19,563 19,581 -2,092 20,000 22 0.89
BPS_RM_2 - 40 40 - 19,628 22 0.88
BPS_RM_3 - 100 100 - 18,082 22 0.81
UHURU_INLET - - 50 - 17,460 22 0.78
ESR_BRANCH 38 - 38 0 372 22 0.60
GSR01_BRANCH 40 - 40 0 1,547 22 1.11
IPITO_BRANCH 4,285 4,212 4,221 -64 622 22 0.44
UHURU_J004N 1,555 1,561 1,563 8 1,244 24 0.81
MAKAMBINI_BRANCH 494 - 494 0 622 24 0.92
CHAPWA_BRANCH 2,664 2,786 2,790 126 622 24 0.92
Station Pumps ER Q m3/h Model Q m3/h ER H (m) Model TDH (m) Diff (m) Shaft kW Motor kW
------------ ----- --------- ------------ -------- ------------- -------- -------- --------
MOMBA_INTAKE 1W+1S 978 978 10 12.1 2.1 43 55
GRIT_TANK 1W+1S 978 978 25 17.4 -7.6 62 75
MOMBA_WTP 3W+1S 304 303 330 334.1 4.1 354 450
NKANGAMO_BPS 2W+1S 455 455 221 188.2 -32.8 299 355
PIPE PRESSURE CLASS - length (m) per PN: ER schedule vs model (working pressure / incl. unprotected surge)
Link Basis PN10 PN16 PN25 PN30 PN40 PN64 > max
----------------- ------------- ------ ------ ------ ------ ----- ---- -----
ABSTRACTION ER 100 - - - - - -
ABSTRACTION model working 100 - - - - - -
ABSTRACTION model + surge 100 - - - - - -
RAW_MAIN ER 1,177 - - - - - -
RAW_MAIN model working 1,078 - - - - - -
RAW_MAIN model + surge 1,078 - - - - - -
WTP_IKANA_RM ER 305 119 4,705 10,798 5,067 - -
WTP_IKANA_RM model working 257 436 6,746 10,776 1,450 - -
WTP_IKANA_RM model + surge 257 - 1,981 11,501 5,926 - -
IKANA_NKANGAMO_GM ER 2,877 13,247 22,380 - - - -
IKANA_NKANGAMO_GM model working 570 18,575 19,784 - - - -
IKANA_NKANGAMO_GM model + surge - 2,371 36,560 - - - -
BPS_RM_1 ER 10,310 7,177 4,185 - - - -
BPS_RM_1 model working 12,023 5,624 1,935 - - - -
BPS_RM_1 model + surge 6,459 5,605 7,518 - - - -
ESR_BRANCH ER 38 - - - - - -
ESR_BRANCH model working 38 - - - - - -
ESR_BRANCH model + surge 38 - - - - - -
GSR01_BRANCH ER - 40 - - - - -
GSR01_BRANCH model working 40 - - - - - -
GSR01_BRANCH model + surge - 40 - - - - -
IPITO_BRANCH ER 4,285 - - - - - -
IPITO_BRANCH model working 3,986 234 - - - - -
IPITO_BRANCH model + surge 2,812 1,409 - - - - -
UHURU_J004N ER 1,555 - - - - - -
UHURU_J004N model working 1,563 - - - - - -
UHURU_J004N model + surge 815 748 - - - - -
MAKAMBINI_BRANCH ER 494 - - - - - -
MAKAMBINI_BRANCH model working 494 - - - - - -
MAKAMBINI_BRANCH model + surge - 494 - - - - -
CHAPWA_BRANCH ER - - 2,664 - - - -
CHAPWA_BRANCH model working 599 1,988 204 - - - -
CHAPWA_BRANCH model + surge - 599 2,191 - - - -
Note: the ER schedule for BPS_RM_1 covers the whole BPS -> Uhuru Park main (21,672 m).
ALIGNMENT CORRECTIONS
P0066: length 82.61 m < straight-line distance 102.46 m -> 102.46 m used
P2160: length 44.56 m < straight-line distance 104.99 m -> 104.99 m used
EPANET steady-state check: Tunduma_Transmission_Main_v1_ER_pumps.inp
----------------------------------------------------------------------------------------------------
PUMP STATIONS (EPANET operating point vs design)
Station pumps Q/pump l/s design ER Q tot m3/h design head m design ER
MOMBA_INTAKE 1 295.7 271.5 271.7 1065 978 9.4 12.1 10
GRIT_TANK 1 341.8 271.5 271.7 1230 978 20.1 17.4 25
MOMBA_WTP 3 83.5 84.2 84.4 902 909 332.5 334.1 330
NKANGAMO_BPS 2 126.3 126.3 126.4 909 909 221.1 188.2 221
PIPELINES (flow and pressure along the route in EPANET)
Link Q l/s design diff % Pmin m Pmax m HGL end design valve
ABSTRACTION 295.7 271.5 8.9 nan nan 1360.8 1360.8
LL_DELIVERY 295.7 271.5 8.9 nan nan 1366.5 1369.0
RAW_MAIN 341.8 271.5 25.9 7.2 15.7 1379.0 1379.0
WTP_IKANA_RM 250.4 252.5 -0.8 6.6 324.8 1667.9 1669.0
IKANA_NKANGAMO_GM 231.5 231.5 -0.0 69.1 209.4 1616.4 1611.7 ACTIVE (controlling)
BPS_RM_1 252.5 252.5 -0.0 38.4 209.3 1740.7 1707.7
BPS_RM_2 247.8 247.8 -0.0 41.5 41.5 1740.6 1707.7
BPS_RM_3 228.3 228.3 0.0 41.0 41.2 1740.5 1707.5
UHURU_INLET 220.5 220.5 -0.0 nan nan 1740.5 1707.5 ACTIVE (controlling)
ESR_BRANCH 4.7 4.7 0.0 nan nan 1740.5 1707.5 ACTIVE (controlling)
GSR01_BRANCH 19.5 19.5 -0.0 nan nan 1740.2 1707.2 ACTIVE (controlling)
IPITO_BRANCH 7.9 7.9 0.0 40.8 129.7 1731.4 1698.4 ACTIVE (controlling)
UHURU_J004N 14.4 14.4 -0.0 1.5 58.3 1691.9 1687.2
MAKAMBINI_BRANCH 7.2 7.2 -0.0 nan nan 1685.4 1680.7 ACTIVE (controlling)
CHAPWA_BRANCH 7.2 7.2 -0.0 62.3 131.2 1655.0 1650.4 ACTIVE (controlling)
Nodes with negative pressure: 0
EPANET steady-state check: Tunduma_Transmission_Main_v1_design_pumps.inp
----------------------------------------------------------------------------------------------------
PUMP STATIONS (EPANET operating point vs design)
Station pumps Q/pump l/s design ER Q tot m3/h design head m design ER
MOMBA_INTAKE 1 327.2 271.5 271.7 1178 978 10.2 12.1 10
GRIT_TANK 1 272.1 271.5 271.7 980 978 17.4 17.4 25
MOMBA_WTP 3 84.5 84.2 84.4 913 909 333.3 334.1 330
NKANGAMO_BPS 2 126.3 126.3 126.4 909 909 188.2 188.2 221
PIPELINES (flow and pressure along the route in EPANET)
Link Q l/s design diff % Pmin m Pmax m HGL end design valve
ABSTRACTION 327.2 271.5 20.5 nan nan 1360.7 1360.8
LL_DELIVERY 327.2 271.5 20.5 nan nan 1366.5 1369.0
RAW_MAIN 272.1 271.5 0.2 7.1 14.8 1379.0 1379.0
WTP_IKANA_RM 253.5 252.5 0.4 6.6 325.5 1667.9 1669.0
IKANA_NKANGAMO_GM 231.5 231.5 -0.0 69.1 209.4 1616.4 1611.7 ACTIVE (controlling)
BPS_RM_1 252.5 252.5 -0.0 5.5 176.4 1707.8 1707.7
BPS_RM_2 247.8 247.8 -0.0 8.6 8.6 1707.7 1707.7
BPS_RM_3 228.3 228.3 -0.0 8.1 8.2 1707.6 1707.5
UHURU_INLET 220.5 220.5 -0.0 nan nan 1707.5 1707.5 ACTIVE (controlling)
ESR_BRANCH 4.7 4.7 0.0 nan nan 1707.6 1707.5 ACTIVE (controlling)
GSR01_BRANCH 19.5 19.5 -0.0 nan nan 1707.3 1707.2 ACTIVE (controlling)
IPITO_BRANCH 7.9 7.9 0.0 7.8 96.8 1698.5 1698.4 ACTIVE (controlling)
UHURU_J004N 14.4 14.4 -0.0 1.5 58.3 1691.9 1687.2
MAKAMBINI_BRANCH 7.2 7.2 -0.0 nan nan 1685.4 1680.7 ACTIVE (controlling)
CHAPWA_BRANCH 7.2 7.2 -0.0 62.3 131.2 1655.0 1650.4 ACTIVE (controlling)
Nodes with negative pressure: 0

## Pipes
Pipe | Name | From | To | Material | DN | ID (mm) | Sized | Length (m) | Hours/day | Q (m3/day) | Q (m3/h) | Q (l/s) | V (m/s) | Friction loss (m) | Minor loss (m) | Total loss (m) | Gradient (m/km) | HGL start (m) | HGL end (m) | Min pressure (m) | Max pressure (m) | Surge dH (m) | Transient min (m) | PN required | PN installed | PN working only | PN incl. surge | PN by chainage (working) | PN by chainage (incl. surge)
ABSTRACTION | Abstraction pipe STEEL DN600-PN10, L = 100 m | MOMBA_RIVER | MOMBA_INTAKE | STEEL | 600 | 600 | given | 100 | 22 | 21505.3763 | 977.5171 | 271.5325 | 0.96035 | 0.16198 | 0.016198 | 0.17817 | 1.7817 | 1361 | 1360.8218 |  | 2.0218 | 97.895 |  | 10 |  | 10 | 10 | PN10 (0-100 m) | PN10 (0-100 m)
LL_DELIVERY | ASSUMED short delivery pipe low-lift PS -> grit tank | MOMBA_INTAKE | GRIT_TANK | STEEL | 600 | 600 | given | 30 | 22 | 21505.3763 | 977.5171 | 271.5325 | 0.96035 | 0.048593 | 0.0048593 | 0.053452 | 1.7817 | 1369.0535 | 1369 |  | 4.3135 | 97.895 |  | 10 |  | 10 | 10 | PN10 (0-30 m) | PN10 (0-30 m)
RAW_MAIN | Raw water pipe STEEL DN600-PN10, L = 1,177 m, V = 0.97 m/s | GRIT_TANK | MOMBA_WTP | STEEL | 600 | 600 | given | 1078.46 | 22 | 21505.3763 | 977.5171 | 271.5325 | 0.96035 | 1.7468 | 0.17468 | 1.9215 | 1.7817 | 1380.9215 | 1379 | 8.3045 | 16.1815 | 97.895 | -89.5905 | 10 |  | 10 | 10 | PN10 (0-1,078 m) | PN10 (0-1,078 m)
WTP_IKANA_RM | Rising main STEEL DN600 PN10/16/25/30/40, L = 20,994 m, V = 0.9 m/s | MOMBA_WTP | IKANA_GBR | STEEL | 600 | 600 | given | 19665.64 | 22 | 20000 | 909.0909 | 252.5253 | 0.89313 | 27.8477 | 2.7848 | 30.6325 | 1.5577 | 1699.6325 | 1669 | 8.8712 | 328.6325 | 91.0423 | -82.1711 | 40 |  | 40 | 40 | PN40 (0-1,450 m), PN30 (1,450-12,227 m), PN25 (12,227-18,973 m), PN16 (18,973-19,408 m), PN10 (19,408-19,666 m) | PN40 (0-5,926 m), PN30 (5,926-17,427 m), PN25 (17,427-19,408 m), PN10 (19,408-19,666 m)
IKANA_NKANGAMO_GM | Gravity main STEEL DN600 PN10/16/25, L = 38,504 m, V = 0.82 m/s | IKANA_GBR | NKANGAMO_BPS | STEEL | 600 | 600 | given | 38930.17 | 24 | 20000 | 833.3333 | 231.4815 | 0.8187 | 46.9227 | 4.6923 | 51.615 | 1.3258 | 1663.3 | 1611.685 | 65.6117 | 205.9184 | 83.4555 | -17.8438 | 25 |  | 25 | 25 | PN10 (0-170 m), PN16 (170-381 m), PN25 (381-7,257 m), PN16 (7,257-9,906 m), PN25 (9,906-10,006 m), PN16 (10,006-10,706 m), PN25 (10,706-12,707 m), PN16 (12,707-13,307 m), PN25 (13,307-14,358 m), PN16 (14,358-19,259 m), PN10 (19,259-19,659 m), PN16 (19,659-24,061 m), PN25 (24,061-24,611 m), PN16 (24,611-25,611 m), PN25 (25,611-34,667 m), PN16 (34,667-35,217 m), PN25 (35,217-35,367 m), PN16 (35,367-38,930 m) | PN16 (0-170 m), PN25 (170-16,609 m), PN16 (16,609-16,709 m), PN25 (16,709-17,509 m), PN16 (17,509-17,809 m), PN25 (17,809-18,659 m), PN16 (18,659-20,459 m), PN25 (20,459-38,930 m)
BPS_RM_1 | Rising main STEEL DN600 PN10/16/25, L = 21,673 m (BPS -> Uhuru Park), V = 0.9 m/s | NKANGAMO_BPS | J-001N | STEEL | 600 | 600 | given | 19581.43 | 22 | 20000 | 909.0909 | 252.5253 | 0.89313 | 27.7285 | 2.7728 | 30.5013 | 1.5577 | 1738.2284 | 1707.7271 | 6.6728 | 183.9284 | 91.0423 | -84.3696 | 25 |  | 25 | 25 | PN25 (0-613 m), PN16 (613-1,513 m), PN25 (1,513-2,553 m), PN16 (2,553-5,495 m), PN25 (5,495-5,776 m), PN16 (5,776-7,558 m), PN10 (7,558-19,581 m) | PN25 (0-7,518 m), PN16 (7,518-10,116 m), PN10 (10,116-10,756 m), PN16 (10,756-13,483 m), PN10 (13,483-16,224 m), PN16 (16,224-16,504 m), PN10 (16,504-19,581 m)
BPS_RM_2 | BPS_RM_2 | J-001N | J-002N | STEEL | 600 | 600 | given | 40.02 | 22 | 19628.48 | 892.2036 | 247.8343 | 0.87653 | 0.054737 | 0.0054737 | 0.06021 | 1.5045 | 1707.7271 | 1707.6669 | 9.6169 | 10.5871 | 89.3511 | -79.7342 | 10 |  | 10 | 10 | PN10 (0-40 m) | PN10 (0-40 m)
BPS_RM_3 | BPS_RM_3 | J-002N | J-003N | STEEL | 600 | 600 | given | 100.25 | 22 | 18081.92 | 821.9055 | 228.3071 | 0.80747 | 0.11778 | 0.011778 | 0.12956 | 1.2924 | 1707.6669 | 1707.5374 | 9.2411 | 9.6169 | 82.311 | -73.07 | 10 |  | 10 | 10 | PN10 (0-100 m) | PN10 (0-100 m)
UHURU_INLET | ASSUMED 50 m from J-003N to the Uhuru Park GBR inlet | J-003N | UHURU_PARK_GBR | STEEL | 600 | 600 | given | 50 | 22 | 17459.82 | 793.6282 | 220.4523 | 0.77969 | 0.055056 | 0.0055056 | 0.060561 | 1.2112 | 1707.5374 | 1707.4768 | 9.3974 | 11.3768 | 79.4791 | -70.0818 | 10 |  | 10 | 10 | PN10 (0-50 m) | PN10 (0-50 m)
ESR_BRANCH | STEEL DN100-PN10, L = 38 m (schematic label DN80) | J-001N | TUNDUMA_ESR | STEEL | 100 | 100 | given | 38 | 22 | 371.52 | 16.8873 | 4.6909 | 0.59727 | 0.20648 | 0.020648 | 0.22713 | 5.977 | 1707.7271 | 1707.5 | 10.5871 | 10.5871 | 60.8833 | -50.2962 | 10 |  | 10 | 10 | PN10 (0-38 m) | PN10 (0-38 m)
GSR01_BRANCH | STEEL DN150-PN16, L = 40 m | J-002N | UHURU_GSR01 | STEEL | 150 | 150 | given | 40 | 22 | 1546.56 | 70.2982 | 19.5273 | 1.105 | 0.42327 | 0.042327 | 0.46559 | 11.6398 | 1707.6669 | 1707.2013 | 9.6169 | 10.0013 | 112.642 | -103.025 | 10 |  | 10 | 16 | PN10 (0-40 m) | PN16 (0-40 m)
IPITO_BRANCH | STEEL DN150-PN10, L = 4,285 m | J-003N | IPITO_GSR02 | STEEL | 150 | 150 | given | 4220.82 | 22 | 622.1 | 28.2773 | 7.8548 | 0.44449 | 8.2694 | 0.82694 | 9.0963 | 2.1551 | 1707.5374 | 1698.441 | 8.9749 | 97.9472 | 45.31 | -36.3351 | 16 |  | 16 | 16 | PN10 (0-2,734 m), PN16 (2,734-2,871 m), PN10 (2,871-3,268 m), PN16 (3,268-3,366 m), PN10 (3,366-4,221 m) | PN10 (0-2,384 m), PN16 (2,384-3,793 m), PN10 (3,793-4,221 m)
UHURU_J004N | Gravity STEEL DN150-PN10, L = 1,555 m, Q = 1,244.2 m3/day | UHURU_PARK_GBR | J-004N | STEEL | 150 | 150 | given | 1563.45 | 24 | 1244.2 | 51.8417 | 14.4005 | 0.8149 | 9.412 | 0.9412 | 10.3532 | 6.622 | 1697.6 | 1687.2468 | -1.9076 | 58.3668 | 83.0682 | -84.9758 | 10 |  | 10 | 16 | PN10 (0-1,563 m) | PN10 (0-815 m), PN16 (815-1,563 m)
MAKAMBINI_BRANCH | STEEL DN100-PN10, L = 494 m (route not surveyed - straight line) | J-004N | MAKAMBINI_GSR03 | STEEL | 100 | 100 | given | 494 | 24 | 622.1 | 25.9208 | 7.2002 | 0.91676 | 5.9354 | 0.59354 | 6.529 | 13.2166 | 1687.2468 | 1680.7178 | 58.3668 | 58.3668 | 93.4518 | -35.085 | 10 |  | 10 | 16 | PN10 (0-494 m) | PN16 (0-494 m)
CHAPWA_BRANCH | STEEL DN100-PN25, L = 2,664 m | J-004N | CHAPWA_GSR04 | STEEL | 100 | 100 | given | 2790.5 | 24 | 622.1 | 25.9208 | 7.2002 | 0.91676 | 33.5281 | 3.3528 | 36.8809 | 13.2166 | 1687.2468 | 1650.3659 | 58.3668 | 127.7559 | 93.4518 | -35.085 | 25 |  | 25 | 25 | PN10 (0-599 m), PN16 (599-2,587 m), PN25 (2,587-2,790 m) | PN16 (0-599 m), PN25 (599-2,790 m)

## Pump stations
Station | Name | Type | Pumps (duty+standby) | Hours/day | Q total (m3/day) | Q total (m3/h) | Q per pump (m3/h) | Q per pump (l/s) | Suction LWL (m) | Delivery HGL (m) | Static+friction (m) | TDH design (m) | TDH at sump TWL (m) | Hydraulic kW/pump | Shaft kW/pump | Motor kW/pump | Input kW (all duty) | Energy (kWh/day) | kWh/m3 | Energy cost/yr | NPSHa (m) | NPSHr (m) | Sump volume (m3) | Sump needed (m3) | Head governed by
MOMBA_INTAKE | Momba Intake - low lift PS | INTAKE | 1w+1s | 22 | 21505.3763 | 977.5171 | 977.5171 | 271.5325 | 1360 | 1369.0535 | 9.0535 | 12.0535 | 8.0535 | 32.1072 | 42.8096 | 55 | 45.5421 | 1001.9265 | 0.04659 | 0 |  |  |  | 162.9195 | inlet of GRIT_TANK (level 1368.0 m + 1.0 m)
GRIT_TANK | Grit tank - high lift PS | SUMP | 1w+1s | 22 | 21505.3763 | 977.5171 | 977.5171 | 271.5325 | 1366.5 | 1380.9215 | 14.4215 | 17.4215 | 15.9215 | 46.4063 | 61.8751 | 75 | 65.8246 | 1448.1408 | 0.067339 | 0 |  |  |  | 162.9195 | inlet of MOMBA_WTP (level 1378.0 m + 1.0 m)
MOMBA_WTP | Momba WTP (20,000 m3/day) | WTP | 3w+1s | 22 | 20000 | 909.0909 | 303.0303 | 84.1751 | 1368.5 | 1699.6325 | 331.1325 | 334.1325 | 329.6325 | 275.9124 | 353.7339 | 450 | 1117.0544 | 24575.196 | 1.2288 | 0 |  |  | 4000 | 151.5152 | inlet of IKANA_GBR (level 1668.0 m + 1.0 m)
NKANGAMO_BPS | Nkangamo BPS | BPS | 2w+1s | 22 | 20000 | 909.0909 | 454.5455 | 126.2626 | 1553 | 1738.2284 | 185.2284 | 188.2284 | 184.2284 | 233.1466 | 298.9059 | 355 | 629.2755 | 13844.0618 | 0.6922 | 0 |  |  | 2000 | 151.5152 | inlet of TUNDUMA_ESR (level 1706.5 m + 1.0 m)

## Tanks
Tank | Name | BWL (m) | TWL (m) | Inlet level (m) | Arrival HGL (m) | Excess head (m) | Inflow (m3/day) | Inflow hours | Outflow (m3/day) | Local demand (m3/day) | Balancing (m3) | Emergency (m3) | Required (m3) | Volume (m3) | Storage (h of outflow)
IKANA_GBR | Ikana (Momba) GBR 3,000 m3 | 1663.3 | 1668 | 1668 | 1663.3 | 0 | 20000 | 22 | 20000 | 0 | 1666.6667 | 0 | 1666.6667 | 3000 | 3.6
UHURU_PARK_GBR | Uhuru Park GBR 5,000 m3 (Tunduma) | 1697.6 | 1702.3 | 1702.3 | 1697.6 | 4.1768 | 17459.82 | 22 | 17459.82 | 16215.62 | 1454.985 | 0 | 1454.985 | 5000 | 6.8729
TUNDUMA_ESR | Existing Tunduma ESR 120 m3 | 1703.5 | 1706.5 | 1706.5 | 1707.5 | 0 | 371.52 | 22 | 371.52 | 371.52 | 30.96 | 0 | 30.96 | 120 | 7.7519
UHURU_GSR01 | Existing Tunduma Uhuru GSR 01 500 m3 | 1698.4 | 1701.4 | 1701.4 | 1707.2013 | 4.8013 | 1546.56 | 22 | 1546.56 | 1546.56 | 128.88 | 0 | 128.88 | 500 | 7.7592
IPITO_GSR02 | Existing Tunduma Ipito GSR 02 | 1681.2 | 1684.2 | 1684.2 | 1698.441 | 13.241 | 622.1 | 22 | 622.1 | 622.1 | 51.8417 | 0 | 51.8417 | 200 | 7.7158
MAKAMBINI_GSR03 | Existing Tunduma Makambini GSR 03 | 1655.7 | 1658.7 | 1658.7 | 1680.7178 | 21.0178 | 622.1 | 24 | 622.1 | 622.1 | 0 | 0 | 0 | 200 | 7.7158
CHAPWA_GSR04 | Existing Tunduma Chapwa GSR 04 | 1521.4 | 1524.4 | 1524.4 | 1650.3659 | 124.9659 | 622.1 | 24 | 622.1 | 622.1 | 0 | 0 | 0 | 200 | 7.7158

## Gravity zones
Zone start | Name | Available head (m) | Required head (m) | Surplus (m) | Status | Governed by
MOMBA_RIVER | Momba (Saisi) River | 1361 | 1360.1782 | 0.82183 | OK | inlet of MOMBA_INTAKE (level 1360.0 m + 0.0 m)
IKANA_GBR | Ikana (Momba) GBR 3,000 m3 | 1663.3 | 1610.115 | 53.185 | OK | inlet of NKANGAMO_BPS (level 1557.5 m + 1.0 m)
UHURU_PARK_GBR | Uhuru Park GBR 5,000 m3 (Tunduma) | 1697.6 | 1701.5076 | -3.9076 | SHORT OF HEAD | pipe UHURU_J004N at 179 m (pipe crown 1698.3 m + 2 m min. pressure)

## Profile points
Pipe | From | To | Chainage in pipe (m) | Ground (m) | HGL (m) | Pressure (m) | Working pressure incl. static (m) | PN working | PN incl. surge
ABSTRACTION | MOMBA_RIVER | MOMBA_INTAKE | 0 | 1359 | 1361 | 2 | 5.5 | 10 | 10
ABSTRACTION | MOMBA_RIVER | MOMBA_INTAKE | 100 | 1358.8 | 1360.8218 | 2.0218 | 5.7 | 10 | 10
LL_DELIVERY | MOMBA_INTAKE | GRIT_TANK | 0 | 1364.74 | 1369.0535 | 4.3135 | 4.3135 | 10 | 10
LL_DELIVERY | MOMBA_INTAKE | GRIT_TANK | 30 | 1364.74 | 1369 | 4.26 | 4.26 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 0 | 1364.74 | 1380.9215 | 16.1815 | 16.1815 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 129.83 | 1364.67 | 1380.6902 | 16.0202 | 16.0202 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 179.83 | 1364.82 | 1380.6011 | 15.7811 | 15.7811 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 229.83 | 1364.88 | 1380.512 | 15.632 | 15.632 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 279.83 | 1365.01 | 1380.4229 | 15.4129 | 15.4129 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 329.83 | 1365.13 | 1380.3339 | 15.2039 | 15.2039 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 379.84 | 1366.17 | 1380.2448 | 14.0748 | 14.0748 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 429.85 | 1367.22 | 1380.1557 | 12.9357 | 12.9357 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 479.88 | 1368.97 | 1380.0665 | 11.0965 | 11.0965 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 529.89 | 1370 | 1379.9774 | 9.9774 | 9.9774 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 578.45 | 1371.27 | 1379.8909 | 8.6209 | 8.6209 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 628.45 | 1370.79 | 1379.8018 | 9.0118 | 9.0118 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 678.45 | 1371.15 | 1379.7127 | 8.5627 | 8.5627 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 728.45 | 1371.17 | 1379.6236 | 8.4536 | 8.4536 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 778.45 | 1371.23 | 1379.5345 | 8.3045 | 8.3045 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 828.45 | 1370.98 | 1379.4455 | 8.4655 | 8.4655 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 878.45 | 1370.9 | 1379.3564 | 8.4564 | 8.4564 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 928.46 | 1370.64 | 1379.2673 | 8.6273 | 8.6273 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 978.46 | 1370.39 | 1379.1782 | 8.7882 | 8.7882 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 1028.46 | 1370.73 | 1379.0891 | 8.3591 | 8.3591 | 10 | 10
RAW_MAIN | GRIT_TANK | MOMBA_WTP | 1078.46 | 1371 | 1379 | 8 | 8 | 10 | 10
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 0 | 1371 | 1699.6325 | 328.6325 | 328.6325 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 50.01 | 1372.01 | 1699.5546 | 327.5446 | 327.5446 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 100.02 | 1372.9 | 1699.4767 | 326.5767 | 326.5767 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 150.03 | 1374.05 | 1699.3988 | 325.3488 | 325.3488 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 200.04 | 1375.12 | 1699.3209 | 324.2009 | 324.2009 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 250.05 | 1375.96 | 1699.243 | 323.283 | 323.283 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 300.08 | 1377.59 | 1699.1651 | 321.5751 | 321.5751 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 350.09 | 1378.75 | 1699.0872 | 320.3372 | 320.3372 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 400.12 | 1380.43 | 1699.0092 | 318.5792 | 318.5792 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 450.15 | 1382.17 | 1698.9313 | 316.7613 | 316.7613 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 500.16 | 1383.17 | 1698.8534 | 315.6834 | 315.6834 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 550.19 | 1385 | 1698.7755 | 313.7755 | 313.7755 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 600.21 | 1386.44 | 1698.6976 | 312.2576 | 312.2576 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 650.22 | 1387.52 | 1698.6197 | 311.0997 | 311.0997 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 700.24 | 1388.6 | 1698.5417 | 309.9417 | 309.9417 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 750.24 | 1389.38 | 1698.4639 | 309.0839 | 309.0839 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 800.24 | 1389.77 | 1698.386 | 308.616 | 308.616 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 850.24 | 1389.84 | 1698.3081 | 308.4681 | 308.4681 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 900.24 | 1389.5 | 1698.2302 | 308.7302 | 308.7302 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 950.25 | 1389.24 | 1698.1523 | 308.9123 | 308.9123 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1000.25 | 1388.74 | 1698.0744 | 309.3344 | 309.3344 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1050.25 | 1388.11 | 1697.9965 | 309.8865 | 309.8865 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1100.26 | 1387.29 | 1697.9186 | 310.6286 | 310.6286 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1150.26 | 1387.02 | 1697.8408 | 310.8208 | 310.8208 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1200.26 | 1386.79 | 1697.7629 | 310.9729 | 310.9729 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1250.26 | 1387.43 | 1697.685 | 310.255 | 310.255 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1300.28 | 1388.49 | 1697.6071 | 309.1171 | 309.1171 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1350.28 | 1389.31 | 1697.5292 | 308.2192 | 308.2192 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1400.3 | 1390.69 | 1697.4513 | 306.7613 | 306.7613 | 40 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1450.32 | 1392.04 | 1697.3734 | 305.3334 | 305.3334 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1500.35 | 1393.79 | 1697.2954 | 303.5054 | 303.5054 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1550.39 | 1395.68 | 1697.2175 | 301.5375 | 301.5375 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1600.4 | 1396.97 | 1697.1396 | 300.1696 | 300.1696 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1650.41 | 1397.78 | 1697.0617 | 299.2817 | 299.2817 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1700.42 | 1398.63 | 1696.9838 | 298.3538 | 298.3538 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1750.42 | 1399.51 | 1696.9059 | 297.3959 | 297.3959 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1800.43 | 1400.08 | 1696.828 | 296.748 | 296.748 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1850.44 | 1401.31 | 1696.7501 | 295.4401 | 295.4401 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1886.63 | 1402.51 | 1696.6937 | 294.1837 | 294.1837 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1936.63 | 1402.65 | 1696.6159 | 293.9659 | 293.9659 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 1986.66 | 1400.99 | 1696.5379 | 295.5479 | 295.5479 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2036.66 | 1401.54 | 1696.46 | 294.92 | 294.92 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2086.68 | 1402.89 | 1696.3821 | 293.4921 | 293.4921 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2136.7 | 1404.29 | 1696.3042 | 292.0142 | 292.0142 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2186.73 | 1405.93 | 1696.2263 | 290.2963 | 290.2963 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2236.7 | 1405.11 | 1696.1485 | 291.0385 | 291.0385 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2339.16 | 1405.27 | 1695.9889 | 290.7189 | 290.7189 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2389.16 | 1404.8 | 1695.911 | 291.111 | 291.111 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2439.25 | 1401.84 | 1695.8329 | 293.9929 | 293.9929 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2489.25 | 1402.02 | 1695.7551 | 293.7351 | 293.7351 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2539.26 | 1402.55 | 1695.6772 | 293.1272 | 293.1272 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2589.26 | 1402.6 | 1695.5993 | 292.9993 | 292.9993 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2626.71 | 1401.77 | 1695.5409 | 293.7709 | 293.7709 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2676.72 | 1402.66 | 1695.463 | 292.803 | 292.803 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2726.72 | 1403.04 | 1695.3852 | 292.3452 | 292.3452 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2776.74 | 1404.15 | 1695.3073 | 291.1573 | 291.1573 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2826.74 | 1404.68 | 1695.2294 | 290.5494 | 290.5494 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2876.75 | 1405.59 | 1695.1515 | 289.5615 | 289.5615 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2926.75 | 1405.78 | 1695.0736 | 289.2936 | 289.2936 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 2976.75 | 1406.4 | 1694.9957 | 288.5957 | 288.5957 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3026.75 | 1406.68 | 1694.9178 | 288.2378 | 288.2378 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3076.76 | 1407.39 | 1694.8399 | 287.4499 | 287.4499 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3126.76 | 1408.13 | 1694.762 | 286.632 | 286.632 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3176.77 | 1409.05 | 1694.6841 | 285.6341 | 285.6341 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3226.78 | 1409.67 | 1694.6062 | 284.9362 | 284.9362 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3276.78 | 1410.26 | 1694.5284 | 284.2684 | 284.2684 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3326.79 | 1411.08 | 1694.4505 | 283.3705 | 283.3705 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3376.79 | 1411.75 | 1694.3726 | 282.6226 | 282.6226 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3426.79 | 1412.23 | 1694.2947 | 282.0647 | 282.0647 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3476.8 | 1413.05 | 1694.2168 | 281.1668 | 281.1668 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3526.8 | 1413.48 | 1694.1389 | 280.6589 | 280.6589 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3576.14 | 1413.95 | 1694.0621 | 280.1121 | 280.1121 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3626.14 | 1414.31 | 1693.9842 | 279.6742 | 279.6742 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3676.14 | 1414.28 | 1693.9063 | 279.6263 | 279.6263 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3726.15 | 1413.98 | 1693.8284 | 279.8484 | 279.8484 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3776.15 | 1413.46 | 1693.7505 | 280.2905 | 280.2905 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3826.15 | 1412.93 | 1693.6726 | 280.7426 | 280.7426 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3876.16 | 1412.1 | 1693.5947 | 281.4947 | 281.4947 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3926.16 | 1411.51 | 1693.5168 | 282.0068 | 282.0068 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 3976.17 | 1410.54 | 1693.4389 | 282.8989 | 282.8989 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4026.18 | 1409.63 | 1693.361 | 283.731 | 283.731 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4076.19 | 1408.78 | 1693.2831 | 284.5031 | 284.5031 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4126.19 | 1408.32 | 1693.2053 | 284.8853 | 284.8853 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4176.2 | 1407.09 | 1693.1274 | 286.0374 | 286.0374 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4226.21 | 1406.2 | 1693.0495 | 286.8495 | 286.8495 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4276.22 | 1405.56 | 1692.9716 | 287.4116 | 287.4116 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4326.23 | 1404.46 | 1692.8937 | 288.4337 | 288.4337 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4376.23 | 1403.9 | 1692.8158 | 288.9158 | 288.9158 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4426.23 | 1403.38 | 1692.7379 | 289.3579 | 289.3579 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4476.23 | 1403.55 | 1692.66 | 289.11 | 289.11 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4526.23 | 1403.36 | 1692.5821 | 289.2221 | 289.2221 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4576.23 | 1403.46 | 1692.5042 | 289.0442 | 289.0442 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4626.23 | 1403.69 | 1692.4264 | 288.7364 | 288.7364 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4676.23 | 1403.7 | 1692.3485 | 288.6485 | 288.6485 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4726.23 | 1403.9 | 1692.2706 | 288.3706 | 288.3706 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4776.24 | 1404.19 | 1692.1927 | 288.0027 | 288.0027 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4826.25 | 1405.34 | 1692.1148 | 286.7748 | 286.7748 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4876.25 | 1404.6 | 1692.0369 | 287.4369 | 287.4369 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4926.25 | 1404.59 | 1691.959 | 287.369 | 287.369 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 4976.25 | 1404.69 | 1691.8812 | 287.1912 | 287.1912 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5026.25 | 1404.94 | 1691.8033 | 286.8633 | 286.8633 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5076.26 | 1405.33 | 1691.7254 | 286.3954 | 286.3954 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5126.26 | 1405.79 | 1691.6475 | 285.8575 | 285.8575 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5176.26 | 1406.25 | 1691.5696 | 285.3196 | 285.3196 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5226.26 | 1406.59 | 1691.4917 | 284.9017 | 284.9017 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5276.26 | 1406.98 | 1691.4138 | 284.4338 | 284.4338 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5326.27 | 1407.78 | 1691.3359 | 283.5559 | 283.5559 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5376.27 | 1408.42 | 1691.2581 | 282.8381 | 282.8381 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5426.28 | 1409.06 | 1691.1802 | 282.1202 | 282.1202 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5476.28 | 1409.5 | 1691.1023 | 281.6023 | 281.6023 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5526.28 | 1410.11 | 1691.0244 | 280.9144 | 280.9144 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5576.29 | 1410.65 | 1690.9465 | 280.2965 | 280.2965 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5626.29 | 1411.08 | 1690.8686 | 279.7886 | 279.7886 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5676.29 | 1411.84 | 1690.7907 | 278.9507 | 278.9507 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5726.3 | 1412.59 | 1690.7128 | 278.1228 | 278.1228 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5776.3 | 1412.85 | 1690.6349 | 277.7849 | 277.7849 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5826.31 | 1413.9 | 1690.557 | 276.657 | 276.657 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5876.31 | 1414.06 | 1690.4792 | 276.4192 | 276.4192 | 30 | 40
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5926.32 | 1414.97 | 1690.4013 | 275.4313 | 275.4313 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 5976.32 | 1415.46 | 1690.3234 | 274.8634 | 274.8634 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6026.35 | 1417.17 | 1690.2454 | 273.0754 | 273.0754 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6076.35 | 1416.66 | 1690.1676 | 273.5076 | 273.5076 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6126.36 | 1417.27 | 1690.0897 | 272.8197 | 272.8197 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6176.36 | 1418.05 | 1690.0118 | 271.9618 | 271.9618 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6226.37 | 1418.72 | 1689.9339 | 271.2139 | 271.2139 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6276.37 | 1419.06 | 1689.856 | 270.796 | 270.796 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6326.38 | 1419.79 | 1689.7781 | 269.9881 | 269.9881 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6376.38 | 1420.39 | 1689.7002 | 269.3102 | 269.3102 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6426.38 | 1420.74 | 1689.6223 | 268.8823 | 268.8823 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6476.38 | 1421.18 | 1689.5445 | 268.3645 | 268.3645 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6526.39 | 1421.83 | 1689.4666 | 267.6366 | 267.6366 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6576.39 | 1421.96 | 1689.3887 | 267.4287 | 267.4287 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6626.39 | 1421.89 | 1689.3108 | 267.4208 | 267.4208 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6676.39 | 1422.77 | 1689.2329 | 266.4629 | 266.4629 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6726.39 | 1422.64 | 1689.155 | 266.515 | 266.515 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6776.4 | 1423.08 | 1689.0771 | 265.9971 | 265.9971 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6826.4 | 1423.47 | 1688.9992 | 265.5292 | 265.5292 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6876.4 | 1423.64 | 1688.9214 | 265.2814 | 265.2814 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6926.4 | 1423.57 | 1688.8435 | 265.2735 | 265.2735 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 6976.4 | 1423.7 | 1688.7656 | 265.0656 | 265.0656 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7026.4 | 1423.25 | 1688.6877 | 265.4377 | 265.4377 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7076.4 | 1423.39 | 1688.6098 | 265.2198 | 265.2198 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7126.4 | 1423.56 | 1688.5319 | 264.9719 | 264.9719 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7176.4 | 1423.39 | 1688.4541 | 265.0641 | 265.0641 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7226.4 | 1423.65 | 1688.3762 | 264.7262 | 264.7262 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7276.41 | 1422.8 | 1688.2983 | 265.4983 | 265.4983 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7326.41 | 1423.4 | 1688.2204 | 264.8204 | 264.8204 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7376.41 | 1423.48 | 1688.1425 | 264.6625 | 264.6625 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7426.42 | 1424.12 | 1688.0646 | 263.9446 | 263.9446 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7476.42 | 1424.7 | 1687.9867 | 263.2867 | 263.2867 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7526.42 | 1424.9 | 1687.9088 | 263.0088 | 263.0088 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7576.43 | 1425.69 | 1687.8309 | 262.1409 | 262.1409 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7626.43 | 1425.77 | 1687.7531 | 261.9831 | 261.9831 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7676.43 | 1426.03 | 1687.6752 | 261.6452 | 261.6452 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7726.43 | 1426.72 | 1687.5973 | 260.8773 | 260.8773 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7776.43 | 1426.58 | 1687.5194 | 260.9394 | 260.9394 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7826.43 | 1426.97 | 1687.4415 | 260.4715 | 260.4715 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7876.43 | 1427.03 | 1687.3636 | 260.3336 | 260.3336 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7926.43 | 1427.27 | 1687.2858 | 260.0158 | 260.0158 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 7976.43 | 1427.15 | 1687.2079 | 260.0579 | 260.0579 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8026.44 | 1427.45 | 1687.13 | 259.68 | 259.68 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8076.44 | 1428.24 | 1687.0521 | 258.8121 | 258.8121 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8126.44 | 1428.27 | 1686.9742 | 258.7042 | 258.7042 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8176.45 | 1427.69 | 1686.8963 | 259.2063 | 259.2063 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8226.45 | 1427.74 | 1686.8184 | 259.0784 | 259.0784 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8276.45 | 1427.57 | 1686.7405 | 259.1705 | 259.1705 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8326.45 | 1427.89 | 1686.6627 | 258.7727 | 258.7727 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8376.45 | 1428.06 | 1686.5848 | 258.5248 | 258.5248 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8426.45 | 1427.16 | 1686.5069 | 259.3469 | 259.3469 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8476.46 | 1426.83 | 1686.429 | 259.599 | 259.599 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8526.46 | 1426.43 | 1686.3511 | 259.9211 | 259.9211 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8576.46 | 1426.23 | 1686.2732 | 260.0432 | 260.0432 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8626.46 | 1426.05 | 1686.1953 | 260.1453 | 260.1453 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8676.46 | 1426.39 | 1686.1175 | 259.7275 | 259.7275 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8726.46 | 1425.84 | 1686.0396 | 260.1996 | 260.1996 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8776.46 | 1425.88 | 1685.9617 | 260.0817 | 260.0817 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8826.46 | 1426.15 | 1685.8838 | 259.7338 | 259.7338 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8876.46 | 1426.03 | 1685.8059 | 259.7759 | 259.7759 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8926.47 | 1426.51 | 1685.728 | 259.218 | 259.218 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 8976.47 | 1426.9 | 1685.6501 | 258.7501 | 258.7501 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9026.47 | 1427.66 | 1685.5723 | 257.9123 | 257.9123 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9076.48 | 1428.35 | 1685.4944 | 257.1444 | 257.1444 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9126.48 | 1428.51 | 1685.4165 | 256.9065 | 256.9065 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9176.48 | 1428.35 | 1685.3386 | 256.9886 | 256.9886 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9226.48 | 1428.71 | 1685.2607 | 256.5507 | 256.5507 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9276.48 | 1429.01 | 1685.1828 | 256.1728 | 256.1728 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9326.48 | 1429.25 | 1685.1049 | 255.8549 | 255.8549 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9376.48 | 1429.13 | 1685.0271 | 255.8971 | 255.8971 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9426.48 | 1429.03 | 1684.9492 | 255.9192 | 255.9192 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9476.48 | 1428.88 | 1684.8713 | 255.9913 | 255.9913 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9526.48 | 1429.06 | 1684.7934 | 255.7334 | 255.7334 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9576.49 | 1428.15 | 1684.7155 | 256.5655 | 256.5655 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9626.49 | 1427.77 | 1684.6376 | 256.8676 | 256.8676 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9676.49 | 1428.09 | 1684.5598 | 256.4698 | 256.4698 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9726.5 | 1427.23 | 1684.4819 | 257.2519 | 257.2519 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9776.5 | 1426.89 | 1684.404 | 257.514 | 257.514 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9826.5 | 1426.77 | 1684.3261 | 257.5561 | 257.5561 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9876.5 | 1426.65 | 1684.2482 | 257.5982 | 257.5982 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9926.5 | 1426.47 | 1684.1703 | 257.7003 | 257.7003 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 9976.5 | 1425.99 | 1684.0924 | 258.1024 | 258.1024 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10026.51 | 1425.61 | 1684.0145 | 258.4045 | 258.4045 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10076.51 | 1425.95 | 1683.9367 | 257.9867 | 257.9867 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10126.52 | 1424.67 | 1683.8588 | 259.1888 | 259.1888 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10176.52 | 1424.81 | 1683.7809 | 258.9709 | 258.9709 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10226.52 | 1424.48 | 1683.703 | 259.223 | 259.223 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10276.53 | 1423.71 | 1683.6251 | 259.9151 | 259.9151 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10326.53 | 1423.42 | 1683.5472 | 260.1272 | 260.1272 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10376.53 | 1423 | 1683.4693 | 260.4693 | 260.4693 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10426.53 | 1423.28 | 1683.3914 | 260.1114 | 260.1114 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10476.54 | 1422.28 | 1683.3135 | 261.0335 | 261.0335 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10526.54 | 1421.97 | 1683.2357 | 261.2657 | 261.2657 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10576.54 | 1421.75 | 1683.1578 | 261.4078 | 261.4078 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10626.55 | 1421.54 | 1683.0799 | 261.5399 | 261.5399 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10676.56 | 1420.28 | 1683.002 | 262.722 | 262.722 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10726.56 | 1420.3 | 1682.9241 | 262.6241 | 262.6241 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10776.56 | 1420.32 | 1682.8462 | 262.5262 | 262.5262 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10826.57 | 1419.32 | 1682.7683 | 263.4483 | 263.4483 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10876.58 | 1418.7 | 1682.6904 | 263.9904 | 263.9904 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10926.58 | 1418.62 | 1682.6125 | 263.9925 | 263.9925 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 10976.58 | 1418.38 | 1682.5346 | 264.1546 | 264.1546 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11026.58 | 1418.34 | 1682.4568 | 264.1168 | 264.1168 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11076.58 | 1418.02 | 1682.3789 | 264.3589 | 264.3589 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11126.58 | 1417.9 | 1682.301 | 264.401 | 264.401 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11176.58 | 1417.64 | 1682.2231 | 264.5831 | 264.5831 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11226.58 | 1417.24 | 1682.1452 | 264.9052 | 264.9052 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11276.61 | 1415.45 | 1682.0673 | 266.6173 | 266.6173 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11326.61 | 1414.94 | 1681.9894 | 267.0494 | 267.0494 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11376.62 | 1415.95 | 1681.9115 | 265.9615 | 265.9615 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11426.62 | 1415.82 | 1681.8336 | 266.0136 | 266.0136 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11476.63 | 1415.31 | 1681.7557 | 266.4457 | 266.4457 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11526.64 | 1416.52 | 1681.6778 | 265.1578 | 265.1578 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11576.65 | 1417.49 | 1681.5999 | 264.1099 | 264.1099 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11626.65 | 1417.51 | 1681.5221 | 264.0121 | 264.0121 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11676.65 | 1417.23 | 1681.4442 | 264.2142 | 264.2142 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11726.65 | 1417.17 | 1681.3663 | 264.1963 | 264.1963 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11776.65 | 1417.72 | 1681.2884 | 263.5684 | 263.5684 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11826.66 | 1418.09 | 1681.2105 | 263.1205 | 263.1205 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11876.66 | 1417.25 | 1681.1326 | 263.8826 | 263.8826 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11926.67 | 1417.78 | 1681.0547 | 263.2747 | 263.2747 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 11976.74 | 1420.44 | 1680.9767 | 260.5367 | 260.5367 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12026.75 | 1421.72 | 1680.8988 | 259.1788 | 259.1788 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12076.78 | 1423.22 | 1680.8209 | 257.6009 | 257.6009 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12126.79 | 1424.25 | 1680.743 | 256.493 | 256.493 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12176.79 | 1425.08 | 1680.6651 | 255.5851 | 255.5851 | 30 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12226.82 | 1426.69 | 1680.5872 | 253.8972 | 253.8972 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12276.84 | 1428.13 | 1680.5093 | 252.3793 | 252.3793 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12326.85 | 1428.99 | 1680.4314 | 251.4414 | 251.4414 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12376.87 | 1430.55 | 1680.3535 | 249.8035 | 249.8035 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12426.88 | 1431.23 | 1680.2756 | 249.0456 | 249.0456 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12476.89 | 1432.37 | 1680.1977 | 247.8277 | 247.8277 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12526.91 | 1433.74 | 1680.1198 | 246.3798 | 246.3798 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12576.93 | 1435.2 | 1680.0418 | 244.8418 | 244.8418 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12626.94 | 1436.22 | 1679.9639 | 243.7439 | 243.7439 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12676.95 | 1437.44 | 1679.886 | 242.446 | 242.446 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12726.96 | 1438.16 | 1679.8081 | 241.6481 | 241.6481 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12776.97 | 1439.03 | 1679.7302 | 240.7002 | 240.7002 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12826.97 | 1439.64 | 1679.6524 | 240.0124 | 240.0124 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12876.99 | 1440.96 | 1679.5744 | 238.6144 | 238.6144 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12926.99 | 1441.15 | 1679.4966 | 238.3466 | 238.3466 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 12976.99 | 1441.81 | 1679.4187 | 237.6087 | 237.6087 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13026.99 | 1442.14 | 1679.3408 | 237.2008 | 237.2008 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13076.99 | 1442.31 | 1679.2629 | 236.9529 | 236.9529 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13126.99 | 1442.32 | 1679.185 | 236.865 | 236.865 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13176.99 | 1442.36 | 1679.1071 | 236.7471 | 236.7471 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13227 | 1441.84 | 1679.0292 | 237.1892 | 237.1892 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13277 | 1441.69 | 1678.9514 | 237.2614 | 237.2614 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13327 | 1441.43 | 1678.8735 | 237.4435 | 237.4435 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13377 | 1441.47 | 1678.7956 | 237.3256 | 237.3256 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13427 | 1440.83 | 1678.7177 | 237.8877 | 237.8877 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13477 | 1440.64 | 1678.6398 | 237.9998 | 237.9998 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13527 | 1440.34 | 1678.5619 | 238.2219 | 238.2219 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13577 | 1440.22 | 1678.4841 | 238.2641 | 238.2641 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13627 | 1440.03 | 1678.4062 | 238.3762 | 238.3762 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13677 | 1440.06 | 1678.3283 | 238.2683 | 238.2683 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13727 | 1440.22 | 1678.2504 | 238.0304 | 238.0304 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13777 | 1440.46 | 1678.1725 | 237.7125 | 237.7125 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13827 | 1440.44 | 1678.0946 | 237.6546 | 237.6546 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13877.01 | 1441.15 | 1678.0167 | 236.8667 | 236.8667 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13927.01 | 1441.24 | 1677.9389 | 236.6989 | 236.6989 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 13977.01 | 1441.44 | 1677.861 | 236.421 | 236.421 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14027.01 | 1441.63 | 1677.7831 | 236.1531 | 236.1531 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14077.01 | 1441.87 | 1677.7052 | 235.8352 | 235.8352 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14127.01 | 1442.42 | 1677.6273 | 235.2073 | 235.2073 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14177.02 | 1442.94 | 1677.5494 | 234.6094 | 234.6094 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14227.02 | 1443.46 | 1677.4715 | 234.0115 | 234.0115 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14277.02 | 1443.63 | 1677.3937 | 233.7637 | 233.7637 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14327.02 | 1444.33 | 1677.3158 | 232.9858 | 232.9858 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14377.03 | 1445 | 1677.2379 | 232.2379 | 232.2379 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14427.03 | 1445.26 | 1677.16 | 231.9 | 231.9 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14477.03 | 1445.77 | 1677.0821 | 231.3121 | 231.3121 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14527.04 | 1446.46 | 1677.0042 | 230.5442 | 230.5442 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14577.04 | 1446.76 | 1676.9263 | 230.1663 | 230.1663 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14627.04 | 1447.02 | 1676.8485 | 229.8285 | 229.8285 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14677.04 | 1447.51 | 1676.7706 | 229.2606 | 229.2606 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14727.04 | 1447.56 | 1676.6927 | 229.1327 | 229.1327 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14777.04 | 1447.95 | 1676.6148 | 228.6648 | 228.6648 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14827.04 | 1447.64 | 1676.5369 | 228.8969 | 228.8969 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14877.05 | 1448.17 | 1676.459 | 228.289 | 228.289 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14927.05 | 1448.38 | 1676.3811 | 228.0011 | 228.0011 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 14977.05 | 1448.59 | 1676.3033 | 227.7133 | 227.7133 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15027.05 | 1448.66 | 1676.2254 | 227.5654 | 227.5654 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15077.05 | 1449.23 | 1676.1475 | 226.9175 | 226.9175 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15127.05 | 1448.92 | 1676.0696 | 227.1496 | 227.1496 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15177.05 | 1448.93 | 1675.9917 | 227.0617 | 227.0617 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15227.05 | 1449.41 | 1675.9138 | 226.5038 | 226.5038 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15277.05 | 1449.59 | 1675.836 | 226.246 | 226.246 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15327.05 | 1449.61 | 1675.7581 | 226.1481 | 226.1481 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15377.05 | 1449.5 | 1675.6802 | 226.1802 | 226.1802 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15427.06 | 1449.84 | 1675.6023 | 225.7623 | 225.7623 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15477.06 | 1449.91 | 1675.5244 | 225.6144 | 225.6144 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15527.06 | 1450.57 | 1675.4465 | 224.8765 | 224.8765 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15577.06 | 1449.94 | 1675.3686 | 225.4286 | 225.4286 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15627.06 | 1450.01 | 1675.2908 | 225.2808 | 225.2808 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15677.07 | 1450.47 | 1675.2129 | 224.7429 | 224.7429 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15727.07 | 1450.34 | 1675.135 | 224.795 | 224.795 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15777.07 | 1450.79 | 1675.0571 | 224.2671 | 224.2671 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15827.07 | 1450.82 | 1674.9792 | 224.1592 | 224.1592 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15877.07 | 1450.87 | 1674.9013 | 224.0313 | 224.0313 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15927.07 | 1451.29 | 1674.8234 | 223.5334 | 223.5334 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 15977.07 | 1451.42 | 1674.7456 | 223.3256 | 223.3256 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16027.07 | 1451.53 | 1674.6677 | 223.1377 | 223.1377 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16077.07 | 1451.77 | 1674.5898 | 222.8198 | 222.8198 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16127.07 | 1451.63 | 1674.5119 | 222.8819 | 222.8819 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16177.07 | 1451.7 | 1674.434 | 222.734 | 222.734 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16227.07 | 1451.75 | 1674.3561 | 222.6061 | 222.6061 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16277.07 | 1451.7 | 1674.2783 | 222.5783 | 222.5783 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16327.07 | 1451.11 | 1674.2004 | 223.0904 | 223.0904 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16377.07 | 1451.1 | 1674.1225 | 223.0225 | 223.0225 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16427.08 | 1450.29 | 1674.0446 | 223.7546 | 223.7546 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16477.08 | 1450 | 1673.9667 | 223.9667 | 223.9667 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16527.08 | 1449.6 | 1673.8888 | 224.2888 | 224.2888 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16577.08 | 1449.54 | 1673.8109 | 224.2709 | 224.2709 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16627.09 | 1449.08 | 1673.733 | 224.653 | 224.653 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16677.09 | 1449.72 | 1673.6552 | 223.9352 | 223.9352 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16727.09 | 1450.14 | 1673.5773 | 223.4373 | 223.4373 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16777.11 | 1451.55 | 1673.4994 | 221.9494 | 221.9494 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16827.11 | 1451.04 | 1673.4215 | 222.3815 | 222.3815 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16877.12 | 1451.93 | 1673.3436 | 221.4136 | 221.4136 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16927.14 | 1453.14 | 1673.2657 | 220.1257 | 220.1257 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 16977.15 | 1454.05 | 1673.1878 | 219.1378 | 219.1378 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17027.16 | 1455.31 | 1673.1099 | 217.7999 | 217.7999 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17077.16 | 1455.08 | 1673.032 | 217.952 | 217.952 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17127.17 | 1455.81 | 1672.9541 | 217.1441 | 217.1441 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17177.17 | 1456.47 | 1672.8762 | 216.4062 | 216.4062 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17227.17 | 1456.36 | 1672.7983 | 216.4383 | 216.4383 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17277.17 | 1456.83 | 1672.7204 | 215.8904 | 215.8904 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17327.17 | 1457.13 | 1672.6426 | 215.5126 | 215.5126 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17377.18 | 1457.37 | 1672.5647 | 215.1947 | 215.1947 | 25 | 30
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17427.18 | 1457.98 | 1672.4868 | 214.5068 | 214.5068 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17477.18 | 1458.45 | 1672.4089 | 213.9589 | 213.9589 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17527.19 | 1459.5 | 1672.331 | 212.831 | 212.831 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17577.19 | 1459.61 | 1672.2531 | 212.6431 | 212.6431 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17627.2 | 1460.42 | 1672.1752 | 211.7552 | 211.7552 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17677.2 | 1461.13 | 1672.0973 | 210.9673 | 210.9673 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17727.21 | 1461.63 | 1672.0194 | 210.3894 | 210.3894 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17777.22 | 1462.6 | 1671.9415 | 209.3415 | 209.3415 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17827.23 | 1463.78 | 1671.8636 | 208.0836 | 208.0836 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17877.27 | 1465.69 | 1671.7857 | 206.0957 | 206.0957 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17927.27 | 1465.95 | 1671.7078 | 205.7578 | 205.7578 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 17977.28 | 1467.21 | 1671.6299 | 204.4199 | 204.4199 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18027.29 | 1468.3 | 1671.552 | 203.252 | 203.252 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18077.3 | 1467.78 | 1671.4741 | 203.6941 | 203.6941 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18127.3 | 1468.39 | 1671.3962 | 203.0062 | 203.0062 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18177.3 | 1468.9 | 1671.3183 | 202.4183 | 202.4183 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18227.31 | 1469.68 | 1671.2404 | 201.5604 | 201.5604 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18277.31 | 1470.41 | 1671.1626 | 200.7526 | 200.7526 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18327.33 | 1471.51 | 1671.0846 | 199.5746 | 199.5746 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18377.34 | 1472.76 | 1671.0067 | 198.2467 | 198.2467 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18427.35 | 1473.3 | 1670.9288 | 197.6288 | 197.6288 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18477.38 | 1475.11 | 1670.8509 | 195.7409 | 195.7409 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18527.39 | 1476.06 | 1670.773 | 194.713 | 194.713 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18577.39 | 1476.46 | 1670.6951 | 194.2351 | 194.2351 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18627.39 | 1476.99 | 1670.6172 | 193.6272 | 193.6272 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18670.95 | 1478.02 | 1670.5494 | 192.5294 | 192.5294 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18721.07 | 1481.47 | 1670.4713 | 189.0013 | 189.0013 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18771.24 | 1485.54 | 1670.3932 | 184.8532 | 184.8532 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18821.37 | 1489.17 | 1670.3151 | 181.1451 | 181.1451 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18871.54 | 1493.3 | 1670.2369 | 176.9369 | 176.9369 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18921.98 | 1499.96 | 1670.1584 | 170.1984 | 170.1984 | 25 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 18972.7 | 1508.44 | 1670.0794 | 161.6394 | 161.6394 | 16 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 19024.41 | 1521.64 | 1669.9988 | 148.3588 | 148.3588 | 16 | 25
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 19408.3 | 1644.76 | 1669.4008 | 24.6408 | 24.6408 | 10 | 10
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 19428.3 | 1645.22 | 1669.3697 | 24.1497 | 24.1497 | 10 | 10
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 19448.42 | 1647.43 | 1669.3384 | 21.9084 | 21.9084 | 10 | 10
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 19468.45 | 1648.39 | 1669.3072 | 20.9172 | 20.9172 | 10 | 10
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 19480.19 | 1648.5 | 1669.2889 | 20.7889 | 20.7889 | 10 | 10
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 19512.89 | 1645.32 | 1669.2379 | 23.9179 | 23.9179 | 10 | 10
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 19542.37 | 1648.45 | 1669.192 | 20.742 | 20.742 | 10 | 10
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 19589.57 | 1654.49 | 1669.1185 | 14.6285 | 14.6285 | 10 | 10
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 19645.61 | 1660.16 | 1669.0312 | 8.8712 | 8.8712 | 10 | 10
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | 19665.64 | 1661.38 | 1669 | 7.62 | 7.62 | 10 | 10
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 0 | 1661.38 | 1663.3 | 1.92 | 6.62 | 10 | 10
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 170.33 | 1577.97 | 1663.0742 | 85.1042 | 90.03 | 10 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 225.08 | 1553.84 | 1663.0016 | 109.1616 | 114.16 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 278 | 1536.5 | 1662.9314 | 126.4314 | 131.5 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 328.96 | 1521.64 | 1662.8639 | 141.2239 | 146.36 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 380.56 | 1508.9 | 1662.7954 | 153.8954 | 159.1 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 431.14 | 1501.26 | 1662.7284 | 161.4684 | 166.74 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 481.46 | 1495.58 | 1662.6617 | 167.0817 | 172.42 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 531.85 | 1489.29 | 1662.5949 | 173.3049 | 178.71 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 581.99 | 1485.64 | 1662.5284 | 176.8884 | 182.36 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 632.16 | 1481.49 | 1662.4619 | 180.9719 | 186.51 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 682.25 | 1478.42 | 1662.3954 | 183.9754 | 189.58 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 721.28 | 1478.99 | 1662.3437 | 183.3537 | 189.01 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 771.29 | 1480.09 | 1662.2774 | 182.1874 | 187.91 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 821.3 | 1480.98 | 1662.2111 | 181.2311 | 187.02 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 871.3 | 1481.62 | 1662.1448 | 180.5248 | 186.38 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 915.78 | 1481.6 | 1662.0858 | 180.4858 | 186.4 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 965.84 | 1479.19 | 1662.0195 | 182.8295 | 188.81 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1009.13 | 1475.95 | 1661.9621 | 186.0121 | 192.05 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1059.16 | 1474.23 | 1661.8957 | 187.6657 | 193.77 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1109.22 | 1471.73 | 1661.8294 | 190.0994 | 196.27 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1159.24 | 1470.55 | 1661.763 | 191.213 | 197.45 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1209.26 | 1468.91 | 1661.6967 | 192.7867 | 199.09 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1259.3 | 1467.05 | 1661.6304 | 194.5804 | 200.95 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1309.31 | 1465.9 | 1661.5641 | 195.6641 | 202.1 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1359.33 | 1464.75 | 1661.4978 | 196.7478 | 203.25 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1409.34 | 1463.52 | 1661.4314 | 197.9114 | 204.48 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1459.36 | 1462.32 | 1661.3651 | 199.0451 | 205.68 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1509.39 | 1460.56 | 1661.2988 | 200.7388 | 207.44 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1559.4 | 1459.49 | 1661.2325 | 201.7425 | 208.51 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1609.42 | 1458.14 | 1661.1662 | 203.0262 | 209.86 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1659.42 | 1457.77 | 1661.0999 | 203.3299 | 210.23 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1709.43 | 1456.57 | 1661.0336 | 204.4636 | 211.43 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1759.44 | 1455.81 | 1660.9673 | 205.1573 | 212.19 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1809.44 | 1455.45 | 1660.901 | 205.451 | 212.55 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1859.44 | 1456.13 | 1660.8347 | 204.7047 | 211.87 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1909.46 | 1454.85 | 1660.7684 | 205.9184 | 213.15 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 1959.46 | 1454.98 | 1660.7021 | 205.7221 | 213.02 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2009.46 | 1455.06 | 1660.6358 | 205.5758 | 212.94 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2059.46 | 1455.29 | 1660.5695 | 205.2795 | 212.71 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2109.46 | 1455.09 | 1660.5032 | 205.4132 | 212.91 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2159.46 | 1455.03 | 1660.4369 | 205.4069 | 212.97 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2209.47 | 1455.91 | 1660.3706 | 204.4606 | 212.09 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2259.47 | 1455.9 | 1660.3043 | 204.4043 | 212.1 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2309.48 | 1456.85 | 1660.238 | 203.388 | 211.15 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2359.48 | 1457.52 | 1660.1717 | 202.6517 | 210.48 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2409.48 | 1458.02 | 1660.1054 | 202.0854 | 209.98 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2459.49 | 1458.63 | 1660.0391 | 201.4091 | 209.37 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2509.49 | 1458.57 | 1659.9728 | 201.4028 | 209.43 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2559.49 | 1458.85 | 1659.9065 | 201.0565 | 209.15 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2609.49 | 1459.21 | 1659.8402 | 200.6302 | 208.79 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2659.49 | 1458.72 | 1659.774 | 201.054 | 209.28 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2709.49 | 1458.55 | 1659.7077 | 201.1577 | 209.45 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2759.5 | 1457.86 | 1659.6414 | 201.7814 | 210.14 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2809.5 | 1458.28 | 1659.5751 | 201.2951 | 209.72 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2859.51 | 1457.24 | 1659.5088 | 202.2688 | 210.76 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2906.15 | 1456.69 | 1659.4469 | 202.7569 | 211.31 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 2956.16 | 1457.15 | 1659.3806 | 202.2306 | 210.85 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3006.16 | 1457.4 | 1659.3143 | 201.9143 | 210.6 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3056.16 | 1457.28 | 1659.248 | 201.968 | 210.72 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3106.16 | 1457.25 | 1659.1817 | 201.9317 | 210.75 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3156.16 | 1457.17 | 1659.1155 | 201.9455 | 210.83 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3206.16 | 1457.4 | 1659.0492 | 201.6492 | 210.6 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3256.16 | 1457.4 | 1658.9829 | 201.5829 | 210.6 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3306.16 | 1457.6 | 1658.9166 | 201.3166 | 210.4 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3356.16 | 1457.83 | 1658.8503 | 201.0203 | 210.17 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3406.16 | 1458.38 | 1658.784 | 200.404 | 209.62 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3456.16 | 1458.62 | 1658.7177 | 200.0977 | 209.38 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3506.16 | 1459.01 | 1658.6514 | 199.6414 | 208.99 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3556.16 | 1459.1 | 1658.5851 | 199.4851 | 208.9 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3606.16 | 1459.35 | 1658.5188 | 199.1688 | 208.65 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3656.16 | 1459.5 | 1658.4525 | 198.9525 | 208.5 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3706.16 | 1459.81 | 1658.3862 | 198.5762 | 208.19 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3756.17 | 1460.2 | 1658.3199 | 198.1199 | 207.8 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3806.17 | 1460.25 | 1658.2536 | 198.0036 | 207.75 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3856.17 | 1460.87 | 1658.1874 | 197.3174 | 207.13 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3906.17 | 1461.26 | 1658.1211 | 196.8611 | 206.74 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 3956.17 | 1461.79 | 1658.0548 | 196.2648 | 206.21 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4006.18 | 1462.44 | 1657.9885 | 195.5485 | 205.56 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4056.19 | 1463.26 | 1657.9222 | 194.6622 | 204.74 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4106.19 | 1463.63 | 1657.8559 | 194.2259 | 204.37 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4156.19 | 1464.38 | 1657.7896 | 193.4096 | 203.62 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4206.2 | 1465.25 | 1657.7233 | 192.4733 | 202.75 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4256.2 | 1465.77 | 1657.657 | 191.887 | 202.23 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4306.2 | 1465.85 | 1657.5907 | 191.7407 | 202.15 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4356.2 | 1466.22 | 1657.5244 | 191.3044 | 201.78 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4406.24 | 1468.09 | 1657.458 | 189.368 | 199.91 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4456.25 | 1467.22 | 1657.3917 | 190.1717 | 200.78 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4506.25 | 1467.77 | 1657.3255 | 189.5555 | 200.23 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4556.25 | 1468.26 | 1657.2592 | 188.9992 | 199.74 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4606.26 | 1469.09 | 1657.1929 | 188.1029 | 198.91 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4656.27 | 1470.21 | 1657.1266 | 186.9166 | 197.79 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4706.28 | 1471.19 | 1657.0602 | 185.8702 | 196.81 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4756.29 | 1472.29 | 1656.9939 | 184.7039 | 195.71 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4806.3 | 1473.24 | 1656.9276 | 183.6876 | 194.76 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4856.32 | 1474.44 | 1656.8613 | 182.4213 | 193.56 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4906.34 | 1475.98 | 1656.795 | 180.815 | 192.02 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 4956.36 | 1477.5 | 1656.7287 | 179.2287 | 190.5 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5006.4 | 1479.29 | 1656.6623 | 177.3723 | 188.71 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5056.41 | 1480.35 | 1656.596 | 176.246 | 187.65 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5106.44 | 1482.04 | 1656.5297 | 174.4897 | 185.96 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5156.45 | 1483.23 | 1656.4634 | 173.2334 | 184.77 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5206.46 | 1484.46 | 1656.3971 | 171.9371 | 183.54 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5256.46 | 1484.45 | 1656.3308 | 171.8808 | 183.55 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5306.47 | 1483.79 | 1656.2645 | 172.4745 | 184.21 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5356.47 | 1483.45 | 1656.1982 | 172.7482 | 184.55 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5406.48 | 1482.3 | 1656.1319 | 173.8319 | 185.7 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5456.51 | 1480.62 | 1656.0656 | 175.4456 | 187.38 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5506.51 | 1480.9 | 1655.9993 | 175.0993 | 187.1 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5556.52 | 1479.85 | 1655.933 | 176.083 | 188.15 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5606.52 | 1479.63 | 1655.8667 | 176.2367 | 188.37 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5656.52 | 1479.65 | 1655.8004 | 176.1504 | 188.35 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5706.52 | 1479.52 | 1655.7341 | 176.2141 | 188.48 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5756.53 | 1480.09 | 1655.6678 | 175.5778 | 187.91 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5806.53 | 1480.36 | 1655.6015 | 175.2415 | 187.64 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5856.53 | 1480.69 | 1655.5352 | 174.8452 | 187.31 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5906.56 | 1482.32 | 1655.4689 | 173.1489 | 185.68 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 5956.56 | 1482.18 | 1655.4026 | 173.2226 | 185.82 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6006.56 | 1482.43 | 1655.3363 | 172.9063 | 185.57 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6056.57 | 1483.41 | 1655.27 | 171.86 | 184.59 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6106.58 | 1484.71 | 1655.2037 | 170.4937 | 183.29 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6156.58 | 1484.37 | 1655.1374 | 170.7674 | 183.63 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6206.6 | 1485.46 | 1655.0711 | 169.6111 | 182.54 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6256.6 | 1486.23 | 1655.0048 | 168.7748 | 181.77 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6306.63 | 1487.82 | 1654.9384 | 167.1184 | 180.18 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6356.64 | 1488.86 | 1654.8721 | 166.0121 | 179.14 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6406.64 | 1489.66 | 1654.8058 | 165.1458 | 178.34 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6456.66 | 1491.02 | 1654.7395 | 163.7195 | 176.98 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6506.72 | 1493.45 | 1654.6732 | 161.2232 | 174.55 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6556.72 | 1493.27 | 1654.6069 | 161.3369 | 174.73 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6606.76 | 1495.16 | 1654.5405 | 159.3805 | 172.84 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6656.78 | 1496.7 | 1654.4742 | 157.7742 | 171.3 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6706.97 | 1497.52 | 1654.4077 | 156.8877 | 170.48 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6757.06 | 1500.5 | 1654.3412 | 153.8412 | 167.5 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6807.09 | 1498.78 | 1654.2749 | 155.4949 | 169.22 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6857.1 | 1499.85 | 1654.2086 | 154.3586 | 168.15 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6907.1 | 1500.29 | 1654.1423 | 153.8523 | 167.71 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 6957.11 | 1501.02 | 1654.076 | 153.056 | 166.98 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7007.12 | 1502.11 | 1654.0097 | 151.8997 | 165.89 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7057.12 | 1502.07 | 1653.9434 | 151.8734 | 165.93 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7107.13 | 1503.01 | 1653.8771 | 150.8671 | 164.99 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7157.15 | 1504.5 | 1653.8108 | 149.3108 | 163.5 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7207.15 | 1504.8 | 1653.7445 | 148.9445 | 163.2 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7257.16 | 1505.86 | 1653.6782 | 147.8182 | 162.14 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7307.16 | 1505.51 | 1653.6119 | 148.1019 | 162.49 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7357.17 | 1506.2 | 1653.5456 | 147.3456 | 161.8 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7407.17 | 1506.09 | 1653.4793 | 147.3893 | 161.91 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7457.17 | 1506.39 | 1653.413 | 147.023 | 161.61 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7507.17 | 1506.92 | 1653.3467 | 146.4267 | 161.08 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7557.17 | 1507.57 | 1653.2804 | 145.7104 | 160.43 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7607.18 | 1508.28 | 1653.2141 | 144.9341 | 159.72 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7657.18 | 1508.41 | 1653.1478 | 144.7378 | 159.59 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7707.23 | 1510.67 | 1653.0815 | 142.4115 | 157.33 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7757.03 | 1512.8 | 1653.0155 | 140.2155 | 155.2 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7807.04 | 1513.85 | 1652.9491 | 139.0991 | 154.15 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7855.04 | 1516.32 | 1652.8855 | 136.5655 | 151.68 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7905.14 | 1519.46 | 1652.8191 | 133.3591 | 148.54 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 7955.14 | 1519.67 | 1652.7528 | 133.0828 | 148.33 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8005.14 | 1519.26 | 1652.6865 | 133.4265 | 148.74 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8055.14 | 1519.22 | 1652.6202 | 133.4002 | 148.78 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8105.14 | 1519.41 | 1652.5539 | 133.1439 | 148.59 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8155.25 | 1518.52 | 1652.4875 | 133.9675 | 149.48 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8205.27 | 1517.19 | 1652.4212 | 135.2312 | 150.81 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8255.28 | 1516.32 | 1652.3549 | 136.0349 | 151.68 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8305.28 | 1516.02 | 1652.2886 | 136.2686 | 151.98 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8355.28 | 1515.95 | 1652.2223 | 136.2723 | 152.05 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8405.28 | 1516.11 | 1652.156 | 136.046 | 151.89 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8455.28 | 1516.21 | 1652.0897 | 135.8797 | 151.79 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8505.28 | 1516.41 | 1652.0234 | 135.6134 | 151.59 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8555.29 | 1517.68 | 1651.9571 | 134.2771 | 150.32 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8605.3 | 1518.59 | 1651.8908 | 133.3008 | 149.41 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8655.32 | 1519.95 | 1651.8245 | 131.8745 | 148.05 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8705.33 | 1520.98 | 1651.7582 | 130.7782 | 147.02 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8755.33 | 1521.54 | 1651.6919 | 130.1519 | 146.46 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8805.34 | 1522.26 | 1651.6256 | 129.3656 | 145.74 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8855.34 | 1521.99 | 1651.5593 | 129.5693 | 146.01 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8905.34 | 1521.79 | 1651.493 | 129.703 | 146.21 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 8955.36 | 1520.51 | 1651.4267 | 130.9167 | 147.49 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9005.37 | 1519.19 | 1651.3604 | 132.1704 | 148.81 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9055.41 | 1517.35 | 1651.294 | 133.944 | 150.65 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9105.44 | 1515.59 | 1651.2277 | 135.6377 | 152.41 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9155.48 | 1513.62 | 1651.1613 | 137.5413 | 154.38 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9205.51 | 1511.82 | 1651.095 | 139.275 | 156.18 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9255.57 | 1509.45 | 1651.0286 | 141.5786 | 158.55 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9305.59 | 1507.98 | 1650.9623 | 142.9823 | 160.02 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9355.59 | 1507.29 | 1650.896 | 143.606 | 160.71 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9405.6 | 1506.43 | 1650.8297 | 144.3997 | 161.57 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9455.61 | 1505.32 | 1650.7634 | 145.4434 | 162.68 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9505.61 | 1505.5 | 1650.6971 | 145.1971 | 162.5 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9555.61 | 1505.33 | 1650.6308 | 145.3008 | 162.67 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9605.61 | 1505.19 | 1650.5645 | 145.3745 | 162.81 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9655.61 | 1505.58 | 1650.4982 | 144.9182 | 162.42 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9705.61 | 1505.55 | 1650.432 | 144.882 | 162.45 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9755.6 | 1505.77 | 1650.3657 | 144.5957 | 162.23 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9805.61 | 1505.16 | 1650.2994 | 145.1394 | 162.84 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9855.61 | 1505.06 | 1650.2331 | 145.1731 | 162.94 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9905.61 | 1505.26 | 1650.1668 | 144.9068 | 162.74 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 9955.61 | 1504.68 | 1650.1005 | 145.4205 | 163.32 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10005.61 | 1505 | 1650.0342 | 145.0342 | 163 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10055.61 | 1505.19 | 1649.9679 | 144.7779 | 162.81 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10105.61 | 1505.52 | 1649.9016 | 144.3816 | 162.48 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10155.62 | 1506.26 | 1649.8353 | 143.5753 | 161.74 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10205.62 | 1506.88 | 1649.769 | 142.889 | 161.12 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10255.62 | 1507.09 | 1649.7027 | 142.6127 | 160.91 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10305.63 | 1507.71 | 1649.6364 | 141.9264 | 160.29 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10355.64 | 1508.62 | 1649.5701 | 140.9501 | 159.38 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10405.64 | 1508.86 | 1649.5038 | 140.6438 | 159.14 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10455.64 | 1509.4 | 1649.4375 | 140.0375 | 158.6 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10505.64 | 1509.44 | 1649.3712 | 139.9312 | 158.56 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10555.64 | 1509.02 | 1649.305 | 140.285 | 158.98 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10605.65 | 1507.99 | 1649.2387 | 141.2487 | 160.01 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10655.66 | 1507.27 | 1649.1723 | 141.9023 | 160.73 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10705.68 | 1505.85 | 1649.106 | 143.256 | 162.15 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10755.69 | 1504.82 | 1649.0397 | 144.2197 | 163.18 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10805.7 | 1503.55 | 1648.9734 | 145.4234 | 164.45 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10855.73 | 1501.87 | 1648.9071 | 147.0371 | 166.13 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10905.75 | 1500.44 | 1648.8408 | 148.4008 | 167.56 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 10955.78 | 1498.82 | 1648.7744 | 149.9544 | 169.18 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11005.78 | 1498.16 | 1648.7081 | 150.5481 | 169.84 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11055.83 | 1496.08 | 1648.6418 | 152.5618 | 171.92 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11105.83 | 1495.32 | 1648.5755 | 153.2555 | 172.68 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11155.97 | 1491.55 | 1648.509 | 156.959 | 176.45 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11206.04 | 1494.1 | 1648.4426 | 154.3426 | 173.9 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11256.04 | 1494.75 | 1648.3763 | 153.6263 | 173.25 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11306.04 | 1494.9 | 1648.31 | 153.41 | 173.1 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11356.05 | 1495.39 | 1648.2437 | 152.8537 | 172.61 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11406.05 | 1494.99 | 1648.1775 | 153.1875 | 173.01 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11456.07 | 1496.57 | 1648.1111 | 151.5411 | 171.43 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11506.07 | 1496.5 | 1648.0448 | 151.5448 | 171.5 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11556.07 | 1496.74 | 1647.9786 | 151.2386 | 171.26 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11606.07 | 1496.66 | 1647.9123 | 151.2523 | 171.34 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11656.08 | 1495.97 | 1647.846 | 151.876 | 172.03 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11706.08 | 1495.51 | 1647.7797 | 152.2697 | 172.49 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11756.08 | 1495.01 | 1647.7134 | 152.7034 | 172.99 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11806.09 | 1495.86 | 1647.6471 | 151.7871 | 172.14 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11856.1 | 1494.72 | 1647.5808 | 152.8608 | 173.28 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11906.1 | 1494.63 | 1647.5145 | 152.8845 | 173.37 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 11956.11 | 1495.08 | 1647.4482 | 152.3682 | 172.92 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12006.11 | 1494.18 | 1647.3819 | 153.2019 | 173.82 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12056.12 | 1493.63 | 1647.3156 | 153.6856 | 174.37 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12106.13 | 1492.7 | 1647.2493 | 154.5493 | 175.3 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12156.14 | 1491.52 | 1647.183 | 155.663 | 176.48 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12206.16 | 1490.17 | 1647.1166 | 156.9466 | 177.83 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12256.22 | 1487.96 | 1647.0503 | 159.0903 | 180.04 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12306.25 | 1486.17 | 1646.9839 | 160.8139 | 181.83 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12356.4 | 1490.04 | 1646.9174 | 156.8774 | 177.96 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12406.44 | 1492.12 | 1646.8511 | 154.7311 | 175.88 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12456.5 | 1494.61 | 1646.7847 | 152.1747 | 173.39 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12506.57 | 1497.13 | 1646.7183 | 149.5883 | 170.87 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12556.63 | 1499.55 | 1646.652 | 147.102 | 168.45 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12606.7 | 1502.29 | 1646.5856 | 144.2956 | 165.71 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12656.72 | 1503.69 | 1646.5193 | 142.8293 | 164.31 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12706.77 | 1505.84 | 1646.4529 | 140.6129 | 162.16 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12756.79 | 1507.47 | 1646.3866 | 138.9166 | 160.53 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12806.83 | 1509.33 | 1646.3202 | 136.9902 | 158.67 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12856.85 | 1510.69 | 1646.2539 | 135.5639 | 157.31 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12906.86 | 1511.95 | 1646.1876 | 134.2376 | 156.05 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 12956.87 | 1512.56 | 1646.1213 | 133.5613 | 155.44 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13006.87 | 1512.99 | 1646.055 | 133.065 | 155.01 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13056.87 | 1512.77 | 1645.9887 | 133.2187 | 155.23 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13106.87 | 1512.15 | 1645.9224 | 133.7724 | 155.85 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13156.88 | 1511.52 | 1645.8561 | 134.3361 | 156.48 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13206.93 | 1509.29 | 1645.7898 | 136.4998 | 158.71 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13256.8 | 1507.79 | 1645.7237 | 137.9337 | 160.21 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13306.86 | 1505.25 | 1645.6573 | 140.4073 | 162.75 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13356.89 | 1503.71 | 1645.591 | 141.881 | 164.29 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13406.95 | 1501.2 | 1645.5246 | 144.3246 | 166.8 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13457.04 | 1498.13 | 1645.4582 | 147.3282 | 169.87 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13507.07 | 1496.48 | 1645.3918 | 148.9118 | 171.52 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13557.12 | 1494.15 | 1645.3255 | 151.1755 | 173.85 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13607.16 | 1492.32 | 1645.2591 | 152.9391 | 175.68 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13657.2 | 1490.24 | 1645.1928 | 154.9528 | 177.76 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13707.24 | 1488.28 | 1645.1265 | 156.8465 | 179.72 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13757.42 | 1483.99 | 1645.0599 | 161.0699 | 184.01 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13807.49 | 1481.47 | 1644.9935 | 163.5235 | 186.53 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13857.62 | 1485.15 | 1644.9271 | 159.7771 | 182.85 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13907.67 | 1487.42 | 1644.8607 | 157.4407 | 180.58 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 13957.7 | 1488.93 | 1644.7944 | 155.8644 | 179.07 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14007.73 | 1490.85 | 1644.7281 | 153.8781 | 177.15 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14057.79 | 1493.22 | 1644.6617 | 151.4417 | 174.78 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14107.8 | 1494.26 | 1644.5954 | 150.3354 | 173.74 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14157.86 | 1496.64 | 1644.529 | 147.889 | 171.36 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14207.92 | 1499.11 | 1644.4626 | 145.3526 | 168.89 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14257.96 | 1501.23 | 1644.3963 | 143.1663 | 166.77 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14308.04 | 1503.99 | 1644.3299 | 140.3399 | 164.01 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14358.08 | 1506.11 | 1644.2635 | 138.1535 | 161.89 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14408.12 | 1508.03 | 1644.1972 | 136.1672 | 159.97 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14458.15 | 1509.77 | 1644.1309 | 134.3609 | 158.23 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14508.19 | 1511.79 | 1644.0645 | 132.2745 | 156.21 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14558.21 | 1513.19 | 1643.9982 | 130.8082 | 154.81 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14608.23 | 1514.48 | 1643.9319 | 129.4519 | 153.52 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14658.23 | 1515 | 1643.8656 | 128.8656 | 153 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14708.23 | 1515.13 | 1643.7993 | 128.6693 | 152.87 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14758.23 | 1515.2 | 1643.733 | 128.533 | 152.8 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14808.25 | 1514.38 | 1643.6667 | 129.2867 | 153.62 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14858.25 | 1513.79 | 1643.6004 | 129.8104 | 154.21 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14908.25 | 1514.21 | 1643.5341 | 129.3241 | 153.79 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 14958.28 | 1512.45 | 1643.4678 | 131.0178 | 155.55 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15008.28 | 1512.28 | 1643.4015 | 131.1215 | 155.72 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15058.29 | 1513.27 | 1643.3352 | 130.0652 | 154.73 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15108.31 | 1514.36 | 1643.2689 | 128.9089 | 153.64 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15158.31 | 1515.01 | 1643.2026 | 128.1926 | 152.99 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15208.33 | 1516.5 | 1643.1363 | 126.6363 | 151.5 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15258.35 | 1517.67 | 1643.0699 | 125.3999 | 150.33 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15308.35 | 1518.28 | 1643.0036 | 124.7236 | 149.72 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15358.38 | 1519.68 | 1642.9373 | 123.2573 | 148.32 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15408.38 | 1519.64 | 1642.871 | 123.231 | 148.36 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15458.38 | 1520.3 | 1642.8047 | 122.5047 | 147.7 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15508.44 | 1522.64 | 1642.7384 | 120.0984 | 145.36 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15558.46 | 1523.95 | 1642.672 | 118.722 | 144.05 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15608.49 | 1525.94 | 1642.6057 | 116.6657 | 142.06 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15658.5 | 1526.77 | 1642.5394 | 115.7694 | 141.23 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15708.54 | 1528.74 | 1642.4731 | 113.7331 | 139.26 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15758.55 | 1529.78 | 1642.4068 | 112.6268 | 138.22 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15808.57 | 1530.96 | 1642.3404 | 111.3804 | 137.04 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15858.58 | 1531.99 | 1642.2741 | 110.2841 | 136.01 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15908.58 | 1532.76 | 1642.2078 | 109.4478 | 135.24 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 15958.58 | 1533.21 | 1642.1415 | 108.9315 | 134.79 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16008.59 | 1533.86 | 1642.0752 | 108.2152 | 134.14 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16058.59 | 1534.25 | 1642.0089 | 107.7589 | 133.75 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16108.67 | 1537.14 | 1641.9426 | 104.8026 | 130.86 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16158.72 | 1539.23 | 1641.8762 | 102.6462 | 128.77 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16208.78 | 1541.72 | 1641.8098 | 100.0898 | 126.28 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16258.87 | 1544.72 | 1641.7434 | 97.0234 | 123.28 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16308.9 | 1546.35 | 1641.6771 | 95.3271 | 121.65 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16358.96 | 1548.89 | 1641.6107 | 92.7207 | 119.11 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16408.99 | 1550.63 | 1641.5444 | 90.9144 | 117.37 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16459.01 | 1552.02 | 1641.4781 | 89.4581 | 115.98 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16509.04 | 1553.77 | 1641.4117 | 87.6417 | 114.23 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16559.06 | 1555.06 | 1641.3454 | 86.2854 | 112.94 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16609.07 | 1556.3 | 1641.2791 | 84.9791 | 111.7 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16659.07 | 1556.42 | 1641.2128 | 84.7928 | 111.58 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16709.07 | 1556.26 | 1641.1465 | 84.8865 | 111.74 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16759.09 | 1555.11 | 1641.0802 | 85.9702 | 112.89 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16809.07 | 1554.38 | 1641.0139 | 86.6339 | 113.62 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16859.08 | 1553.49 | 1640.9476 | 87.4576 | 114.51 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16909.1 | 1551.98 | 1640.8813 | 88.9013 | 116.02 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 16959.1 | 1551.82 | 1640.815 | 88.995 | 116.18 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17009.1 | 1551.62 | 1640.7487 | 89.1287 | 116.38 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17059.1 | 1551.52 | 1640.6824 | 89.1624 | 116.48 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17109.1 | 1551.44 | 1640.6161 | 89.1761 | 116.56 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17159.1 | 1551.48 | 1640.5499 | 89.0699 | 116.52 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17209.1 | 1551.51 | 1640.4836 | 88.9736 | 116.49 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17259.12 | 1552.9 | 1640.4172 | 87.5172 | 115.1 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17309.13 | 1553.65 | 1640.3509 | 86.7009 | 114.35 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17359.13 | 1554.18 | 1640.2846 | 86.1046 | 113.82 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17409.14 | 1555.36 | 1640.2183 | 84.8583 | 112.64 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17459.14 | 1555.36 | 1640.1521 | 84.7921 | 112.64 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17509.15 | 1555.88 | 1640.0857 | 84.2057 | 112.12 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17559.15 | 1556.34 | 1640.0195 | 83.6795 | 111.66 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17609.15 | 1556.81 | 1639.9532 | 83.1432 | 111.19 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17659.15 | 1557.03 | 1639.8869 | 82.8569 | 110.97 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17709.15 | 1556.81 | 1639.8206 | 83.0106 | 111.19 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17759.16 | 1556.22 | 1639.7543 | 83.5343 | 111.78 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17809.16 | 1555.76 | 1639.688 | 83.928 | 112.24 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17859.16 | 1555.46 | 1639.6217 | 84.1617 | 112.54 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17909.16 | 1555.44 | 1639.5554 | 84.1154 | 112.56 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 17959.19 | 1553.6 | 1639.4891 | 85.8891 | 114.4 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18009.19 | 1553.34 | 1639.4228 | 86.0828 | 114.66 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18059.2 | 1552.84 | 1639.3565 | 86.5165 | 115.16 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18109.23 | 1551.07 | 1639.2901 | 88.2201 | 116.93 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18159.24 | 1552.1 | 1639.2238 | 87.1238 | 115.9 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18209.4 | 1548.1 | 1639.1573 | 91.0573 | 119.9 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18259.4 | 1548.27 | 1639.091 | 90.821 | 119.73 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18309.4 | 1548.29 | 1639.0247 | 90.7347 | 119.71 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18359.4 | 1548.03 | 1638.9585 | 90.9285 | 119.97 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18409.4 | 1548.72 | 1638.8922 | 90.1722 | 119.28 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18459.43 | 1550.25 | 1638.8258 | 88.5758 | 117.75 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18509.53 | 1553.48 | 1638.7594 | 85.2794 | 114.52 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18559.53 | 1554.11 | 1638.6931 | 84.5831 | 113.89 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18608.66 | 1554.92 | 1638.628 | 83.708 | 113.08 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18658.69 | 1556.65 | 1638.5616 | 81.9116 | 111.35 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18708.7 | 1557.52 | 1638.4953 | 80.9753 | 110.48 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18758.71 | 1558.36 | 1638.429 | 80.069 | 109.64 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18808.73 | 1559.78 | 1638.3627 | 78.5827 | 108.22 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18858.73 | 1560.6 | 1638.2964 | 77.6964 | 107.4 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18908.74 | 1561.11 | 1638.2301 | 77.1201 | 106.89 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 18958.74 | 1561.81 | 1638.1638 | 76.3538 | 106.19 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19008.76 | 1563.24 | 1638.0975 | 74.8575 | 104.76 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19058.77 | 1564.03 | 1638.0312 | 74.0012 | 103.97 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19108.77 | 1564.22 | 1637.9649 | 73.7449 | 103.78 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19158.78 | 1565.2 | 1637.8986 | 72.6986 | 102.8 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19208.78 | 1565.76 | 1637.8323 | 72.0723 | 102.24 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19258.79 | 1566.53 | 1637.766 | 71.236 | 101.47 | 10 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19308.79 | 1566.8 | 1637.6997 | 70.8997 | 101.2 | 10 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19358.79 | 1567.53 | 1637.6334 | 70.1034 | 100.47 | 10 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19408.79 | 1567.64 | 1637.5671 | 69.9271 | 100.36 | 10 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19458.79 | 1567.72 | 1637.5008 | 69.7808 | 100.28 | 10 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19508.79 | 1567.58 | 1637.4346 | 69.8546 | 100.42 | 10 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19558.79 | 1567.58 | 1637.3683 | 69.7883 | 100.42 | 10 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19608.79 | 1567.13 | 1637.302 | 70.172 | 100.87 | 10 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19658.79 | 1567.05 | 1637.2357 | 70.1857 | 100.95 | 10 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19708.81 | 1565.87 | 1637.1694 | 71.2994 | 102.13 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19758.82 | 1564.65 | 1637.1031 | 72.4531 | 103.35 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19808.82 | 1564.66 | 1637.0368 | 72.3768 | 103.34 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19858.84 | 1563.47 | 1636.9704 | 73.5004 | 104.53 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19908.84 | 1562.67 | 1636.9042 | 74.2342 | 105.33 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 19958.84 | 1562.8 | 1636.8379 | 74.0379 | 105.2 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20008.85 | 1562.3 | 1636.7716 | 74.4716 | 105.7 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20058.86 | 1561.11 | 1636.7052 | 75.5952 | 106.89 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20108.86 | 1561.04 | 1636.639 | 75.599 | 106.96 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20158.86 | 1560.71 | 1636.5727 | 75.8627 | 107.29 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20208.86 | 1560.44 | 1636.5064 | 76.0664 | 107.56 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20258.86 | 1560.71 | 1636.4401 | 75.7301 | 107.29 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20308.89 | 1559.06 | 1636.3737 | 77.3137 | 108.94 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20358.9 | 1558.17 | 1636.3074 | 78.1374 | 109.83 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20408.91 | 1556.96 | 1636.2411 | 79.2811 | 111.04 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20458.91 | 1556.82 | 1636.1748 | 79.3548 | 111.18 | 16 | 16
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20508.94 | 1555.15 | 1636.1085 | 80.9585 | 112.85 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20559.02 | 1552.39 | 1636.0421 | 83.6521 | 115.61 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20609.02 | 1552.22 | 1635.9758 | 83.7558 | 115.78 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20659.04 | 1550.58 | 1635.9095 | 85.3295 | 117.42 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20709.05 | 1550.16 | 1635.8432 | 85.6832 | 117.84 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20759.25 | 1545.6 | 1635.7766 | 90.1766 | 122.4 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20809.25 | 1545.32 | 1635.7104 | 90.3904 | 122.68 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20859.34 | 1542.38 | 1635.6439 | 93.2639 | 125.62 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20909.43 | 1539.36 | 1635.5775 | 96.2175 | 128.64 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 20959.48 | 1537.19 | 1635.5112 | 98.3212 | 130.81 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21009.51 | 1535.47 | 1635.4448 | 99.9748 | 132.53 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21059.57 | 1533 | 1635.3785 | 102.3785 | 135 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21109.65 | 1530.13 | 1635.3121 | 105.1821 | 137.87 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21159.68 | 1528.57 | 1635.2457 | 106.6757 | 139.43 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21209.78 | 1525.29 | 1635.1793 | 109.8893 | 142.71 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21259.82 | 1523.37 | 1635.113 | 111.743 | 144.63 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21309.88 | 1520.94 | 1635.0466 | 114.1066 | 147.06 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21359.93 | 1518.78 | 1634.9802 | 116.2002 | 149.22 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21409.97 | 1516.7 | 1634.9139 | 118.2139 | 151.3 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21460.03 | 1514.28 | 1634.8475 | 120.5675 | 153.72 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21510.05 | 1512.7 | 1634.7812 | 122.0812 | 155.3 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21560.09 | 1510.74 | 1634.7149 | 123.9749 | 157.26 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21610.22 | 1507.11 | 1634.6484 | 127.5384 | 160.89 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21660.23 | 1508.18 | 1634.5821 | 126.4021 | 159.82 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21710.25 | 1509.51 | 1634.5158 | 125.0058 | 158.49 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21760.26 | 1510.18 | 1634.4495 | 124.2695 | 157.82 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21810.32 | 1512.72 | 1634.3831 | 121.6631 | 155.28 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21860.33 | 1513.66 | 1634.3168 | 120.6568 | 154.34 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21910.39 | 1516.21 | 1634.2504 | 118.0404 | 151.79 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 21960.42 | 1517.65 | 1634.1841 | 116.5341 | 150.35 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22010.44 | 1519.3 | 1634.1178 | 114.8178 | 148.7 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22060.48 | 1521.12 | 1634.0514 | 112.9314 | 146.88 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22110.49 | 1522.41 | 1633.9851 | 111.5751 | 145.59 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22160.5 | 1523.28 | 1633.9188 | 110.6388 | 144.72 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22210.52 | 1524.6 | 1633.8525 | 109.2525 | 143.4 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22260.53 | 1525.48 | 1633.7862 | 108.3062 | 142.52 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22310.54 | 1526.89 | 1633.7199 | 106.8299 | 141.11 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22360.56 | 1528.09 | 1633.6536 | 105.5636 | 139.91 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22410.56 | 1528.65 | 1633.5873 | 104.9373 | 139.35 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22460.57 | 1529.36 | 1633.521 | 104.161 | 138.64 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22510.58 | 1530.27 | 1633.4547 | 103.1847 | 137.73 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22560.58 | 1530.48 | 1633.3884 | 102.9084 | 137.52 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22610.58 | 1530.85 | 1633.3221 | 102.4721 | 137.15 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22660.58 | 1531.23 | 1633.2558 | 102.0258 | 136.77 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22710.58 | 1531.49 | 1633.1895 | 101.6995 | 136.51 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22760.58 | 1530.93 | 1633.1232 | 102.1932 | 137.07 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22810.58 | 1531.03 | 1633.0569 | 102.0269 | 136.97 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22860.58 | 1530.71 | 1632.9906 | 102.2806 | 137.29 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22910.58 | 1530.7 | 1632.9243 | 102.2243 | 137.3 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 22960.58 | 1530.42 | 1632.858 | 102.438 | 137.58 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23010.59 | 1530.12 | 1632.7917 | 102.6717 | 137.88 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23060.59 | 1529.99 | 1632.7254 | 102.7354 | 138.01 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23110.59 | 1529.54 | 1632.6592 | 103.1192 | 138.46 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23160.59 | 1529.26 | 1632.5929 | 103.3329 | 138.74 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23210.59 | 1528.86 | 1632.5266 | 103.6666 | 139.14 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23260.61 | 1527.58 | 1632.4603 | 104.8803 | 140.42 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23310.61 | 1526.73 | 1632.394 | 105.664 | 141.27 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23360.62 | 1525.86 | 1632.3277 | 106.4677 | 142.14 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23410.65 | 1524.23 | 1632.2613 | 108.0313 | 143.77 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23460.66 | 1522.93 | 1632.195 | 109.265 | 145.07 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23510.68 | 1521.79 | 1632.1287 | 110.3387 | 146.21 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23560.74 | 1519.29 | 1632.0623 | 112.7723 | 148.71 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23610.76 | 1517.91 | 1631.996 | 114.086 | 150.09 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23660.79 | 1516.18 | 1631.9297 | 115.7497 | 151.82 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23710.81 | 1514.68 | 1631.8634 | 117.1834 | 153.32 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23760.84 | 1513 | 1631.797 | 118.797 | 155 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23810.86 | 1511.44 | 1631.7307 | 120.2907 | 156.56 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23860.86 | 1511.39 | 1631.6644 | 120.2744 | 156.61 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23910.91 | 1509.22 | 1631.5981 | 122.3781 | 158.78 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 23960.94 | 1507.63 | 1631.5317 | 123.9017 | 160.37 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24010.96 | 1506.03 | 1631.4654 | 125.4354 | 161.97 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24060.97 | 1504.92 | 1631.3991 | 126.4791 | 163.08 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24111.01 | 1502.99 | 1631.3328 | 128.3428 | 165.01 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24161.04 | 1501.33 | 1631.2664 | 129.9364 | 166.67 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24211.07 | 1499.56 | 1631.2001 | 131.6401 | 168.44 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24261.1 | 1497.98 | 1631.1338 | 133.1538 | 170.02 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24311.1 | 1498.08 | 1631.0675 | 132.9875 | 169.92 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24361.1 | 1497.88 | 1631.0012 | 133.1212 | 170.12 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24411.11 | 1498.9 | 1630.9349 | 132.0349 | 169.1 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24461.13 | 1500.53 | 1630.8686 | 130.3386 | 167.47 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24511.18 | 1502.77 | 1630.8022 | 128.0322 | 165.23 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24561.21 | 1504.35 | 1630.7359 | 126.3859 | 163.65 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24611.25 | 1506.36 | 1630.6695 | 124.3095 | 161.64 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24661.28 | 1508 | 1630.6032 | 122.6032 | 160 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24711.31 | 1509.91 | 1630.5369 | 120.6269 | 158.09 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24761.32 | 1510.79 | 1630.4706 | 119.6806 | 157.21 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24811.35 | 1512.41 | 1630.4042 | 117.9942 | 155.59 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24861.35 | 1513.04 | 1630.3379 | 117.2979 | 154.96 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24911.35 | 1513.7 | 1630.2716 | 116.5716 | 154.3 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 24961.36 | 1514.35 | 1630.2053 | 115.8553 | 153.65 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25011.36 | 1514.58 | 1630.139 | 115.559 | 153.42 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25061.36 | 1514.12 | 1630.0728 | 115.9528 | 153.88 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25111.36 | 1514.22 | 1630.0065 | 115.7865 | 153.78 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25161.36 | 1513.69 | 1629.9402 | 116.2502 | 154.31 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25211.37 | 1514.32 | 1629.8739 | 115.5539 | 153.68 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25261.37 | 1513.65 | 1629.8076 | 116.1576 | 154.35 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25311.37 | 1513.2 | 1629.7413 | 116.5413 | 154.8 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25361.38 | 1512.67 | 1629.675 | 117.005 | 155.33 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25411.39 | 1511.77 | 1629.6087 | 117.8387 | 156.23 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25461.39 | 1510.88 | 1629.5424 | 118.6624 | 157.12 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25511.42 | 1509.27 | 1629.4761 | 120.2061 | 158.73 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25561.44 | 1507.8 | 1629.4097 | 121.6097 | 160.2 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25611.45 | 1506.72 | 1629.3434 | 122.6234 | 161.28 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25661.53 | 1504.02 | 1629.277 | 125.257 | 163.98 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25711.56 | 1502.3 | 1629.2107 | 126.9107 | 165.7 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25761.59 | 1500.42 | 1629.1444 | 128.7244 | 167.58 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25811.64 | 1498.26 | 1629.078 | 130.818 | 169.74 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25861.73 | 1495.2 | 1629.0116 | 133.8116 | 172.8 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25911.77 | 1493.26 | 1628.9453 | 135.6853 | 174.74 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 25961.86 | 1490.25 | 1628.8788 | 138.6288 | 177.75 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26011.99 | 1486.64 | 1628.8124 | 142.1724 | 181.36 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26062.21 | 1481.88 | 1628.7458 | 146.8658 | 186.12 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26112.37 | 1477.98 | 1628.6793 | 150.6993 | 190.02 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26162.37 | 1478.28 | 1628.613 | 150.333 | 189.72 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26212.77 | 1484.65 | 1628.5462 | 143.8962 | 183.35 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26262.88 | 1488.01 | 1628.4797 | 140.4697 | 179.99 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26312.2 | 1489.9 | 1628.4143 | 138.5143 | 178.1 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26362.23 | 1491.66 | 1628.348 | 136.688 | 176.34 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26412.26 | 1493.37 | 1628.2817 | 134.9117 | 174.63 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26462.28 | 1494.7 | 1628.2154 | 133.5154 | 173.3 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26512.3 | 1495.98 | 1628.149 | 132.169 | 172.02 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26562.3 | 1496.79 | 1628.0828 | 131.2928 | 171.21 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26612.31 | 1497.47 | 1628.0165 | 130.5465 | 170.53 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26662.31 | 1497.04 | 1627.9502 | 130.9102 | 170.96 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26712.31 | 1496.67 | 1627.8839 | 131.2139 | 171.33 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26762.35 | 1494.61 | 1627.8175 | 133.2075 | 173.39 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26812.35 | 1494.1 | 1627.7512 | 133.6512 | 173.9 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26862.37 | 1492.83 | 1627.6849 | 134.8549 | 175.17 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26912.4 | 1490.99 | 1627.6186 | 136.6286 | 177.01 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 26962.43 | 1489.45 | 1627.5522 | 138.1022 | 178.55 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27012.46 | 1487.78 | 1627.4859 | 139.7059 | 180.22 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27062.51 | 1485.42 | 1627.4196 | 141.9996 | 182.58 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27112.54 | 1483.77 | 1627.3532 | 143.5832 | 184.23 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27162.58 | 1481.7 | 1627.2869 | 145.5869 | 186.3 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27212.6 | 1480.4 | 1627.2206 | 146.8206 | 187.6 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27262.61 | 1481.23 | 1627.1543 | 145.9243 | 186.77 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27312.62 | 1482.36 | 1627.088 | 144.728 | 185.64 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27362.65 | 1484.1 | 1627.0216 | 142.9216 | 183.9 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27412.66 | 1485.12 | 1626.9553 | 141.8353 | 182.88 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27462.66 | 1485.88 | 1626.889 | 141.009 | 182.12 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27512.66 | 1485.77 | 1626.8227 | 141.0527 | 182.23 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27562.67 | 1486.15 | 1626.7564 | 140.6064 | 181.85 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27612.67 | 1486.36 | 1626.6901 | 140.3301 | 181.64 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27662.68 | 1485.02 | 1626.6238 | 141.6038 | 182.98 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27712.69 | 1484.73 | 1626.5575 | 141.8275 | 183.27 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27762.71 | 1483.13 | 1626.4912 | 143.3612 | 184.87 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27812.75 | 1481.19 | 1626.4249 | 145.2349 | 186.81 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27862.76 | 1480.11 | 1626.3586 | 146.2486 | 187.89 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27912.82 | 1477.71 | 1626.2922 | 148.5822 | 190.29 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 27962.86 | 1475.6 | 1626.2258 | 150.6258 | 192.4 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28012.91 | 1473.44 | 1626.1595 | 152.7195 | 194.56 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28062.92 | 1474.21 | 1626.0932 | 151.8832 | 193.79 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28112.95 | 1476.18 | 1626.0268 | 149.8468 | 191.82 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28162.98 | 1477.65 | 1625.9605 | 148.3105 | 190.35 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28213.02 | 1479.75 | 1625.8942 | 146.1442 | 188.25 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28263.08 | 1482.24 | 1625.8278 | 143.5878 | 185.76 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28313.09 | 1482.91 | 1625.7615 | 142.8515 | 185.09 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28363.16 | 1485.61 | 1625.6951 | 140.0851 | 182.39 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28413.17 | 1486.86 | 1625.6288 | 138.7688 | 181.14 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28463.18 | 1487.42 | 1625.5625 | 138.1425 | 180.58 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28513.18 | 1487.89 | 1625.4962 | 137.6062 | 180.11 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28563.18 | 1488.42 | 1625.4299 | 137.0099 | 179.58 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28613.18 | 1488.42 | 1625.3636 | 136.9436 | 179.58 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28663.2 | 1489.54 | 1625.2973 | 135.7573 | 178.46 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28713.2 | 1489.61 | 1625.231 | 135.621 | 178.39 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28763.2 | 1488.99 | 1625.1647 | 136.1747 | 179.01 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28813.2 | 1490.18 | 1625.0984 | 134.9184 | 177.82 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28863.21 | 1489.32 | 1625.0321 | 135.7121 | 178.68 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28913.21 | 1488.68 | 1624.9658 | 136.2858 | 179.32 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 28963.22 | 1487.76 | 1624.8995 | 137.1395 | 180.24 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29013.24 | 1486.51 | 1624.8332 | 138.3232 | 181.49 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29063.24 | 1485.76 | 1624.7669 | 139.0069 | 182.24 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29113.26 | 1484.7 | 1624.7006 | 140.0006 | 183.3 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29163.32 | 1482.07 | 1624.6342 | 142.5642 | 185.93 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29213.33 | 1482.43 | 1624.5679 | 142.1379 | 185.57 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29263.34 | 1481.16 | 1624.5016 | 143.3416 | 186.84 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29313.34 | 1481.06 | 1624.4353 | 143.3753 | 186.94 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29363.36 | 1482.48 | 1624.369 | 141.889 | 185.52 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29413.37 | 1483.39 | 1624.3027 | 140.9127 | 184.61 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29463.39 | 1484.59 | 1624.2364 | 139.6464 | 183.41 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29513.39 | 1485.32 | 1624.1701 | 138.8501 | 182.68 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29563.39 | 1485.8 | 1624.1038 | 138.3038 | 182.2 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29613.39 | 1486.25 | 1624.0375 | 137.7875 | 181.75 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29663.4 | 1486 | 1623.9712 | 137.9712 | 182 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29713.4 | 1485.31 | 1623.9049 | 138.5949 | 182.69 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29763.4 | 1484.68 | 1623.8386 | 139.1586 | 183.32 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29813.41 | 1485.13 | 1623.7723 | 138.6423 | 182.87 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29863.41 | 1485.03 | 1623.706 | 138.676 | 182.97 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29913.41 | 1484.59 | 1623.6397 | 139.0497 | 183.41 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 29963.42 | 1485.54 | 1623.5734 | 138.0334 | 182.46 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30013.42 | 1485.53 | 1623.5071 | 137.9771 | 182.47 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30063.42 | 1485.93 | 1623.4408 | 137.5108 | 182.07 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30113.42 | 1486.16 | 1623.3746 | 137.2146 | 181.84 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30163.42 | 1485.41 | 1623.3083 | 137.8983 | 182.59 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30213.43 | 1485.32 | 1623.242 | 137.922 | 182.68 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30263.43 | 1485.04 | 1623.1757 | 138.1357 | 182.96 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30313.43 | 1484.14 | 1623.1094 | 138.9694 | 183.86 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30363.45 | 1482.74 | 1623.0431 | 140.3031 | 185.26 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30413.28 | 1481.99 | 1622.977 | 140.987 | 186.01 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30463.28 | 1481.81 | 1622.9107 | 141.1007 | 186.19 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30513.32 | 1479.86 | 1622.8444 | 142.9844 | 188.14 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30563.35 | 1477.98 | 1622.778 | 144.798 | 190.02 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30613.38 | 1476.41 | 1622.7117 | 146.3017 | 191.59 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30663.42 | 1474.27 | 1622.6453 | 148.3753 | 193.73 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30713.49 | 1471.7 | 1622.579 | 150.879 | 196.3 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30763.56 | 1469.11 | 1622.5126 | 153.4026 | 198.89 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30813.58 | 1467.61 | 1622.4463 | 154.8363 | 200.39 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30863.67 | 1464.52 | 1622.3798 | 157.8598 | 203.48 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30913.75 | 1461.71 | 1622.3134 | 160.6034 | 206.29 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 30963.94 | 1457.42 | 1622.2469 | 164.8269 | 210.58 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31014.01 | 1454.73 | 1622.1805 | 167.4505 | 213.27 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31064.27 | 1449.62 | 1622.1139 | 172.4939 | 218.38 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31114.29 | 1451.07 | 1622.0476 | 170.9776 | 216.93 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31164.44 | 1454.9 | 1621.9811 | 167.0811 | 213.1 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31214.49 | 1457.26 | 1621.9147 | 164.6547 | 210.74 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31264.56 | 1459.82 | 1621.8483 | 162.0283 | 208.18 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31314.74 | 1464.12 | 1621.7818 | 157.6618 | 203.88 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31364.89 | 1467.95 | 1621.7153 | 153.7653 | 200.05 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31415.03 | 1471.77 | 1621.6488 | 149.8788 | 196.23 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31465.2 | 1475.8 | 1621.5823 | 145.7823 | 192.2 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31515.32 | 1479.36 | 1621.5159 | 142.1559 | 188.64 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31565.38 | 1481.71 | 1621.4495 | 139.7395 | 186.29 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31615.49 | 1485 | 1621.3831 | 136.3831 | 183 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31665.6 | 1488.41 | 1621.3166 | 132.9066 | 179.59 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31715.6 | 1488.55 | 1621.2503 | 132.7003 | 179.45 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31765.64 | 1490.54 | 1621.184 | 130.644 | 177.46 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31815.68 | 1492.57 | 1621.1176 | 128.5476 | 175.43 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31865.73 | 1494.78 | 1621.0513 | 126.2713 | 173.22 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31915.73 | 1494.94 | 1620.985 | 126.045 | 173.06 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 31965.75 | 1496.18 | 1620.9187 | 124.7387 | 171.82 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32015.75 | 1496.57 | 1620.8524 | 124.2824 | 171.43 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32065.75 | 1496.37 | 1620.7861 | 124.4161 | 171.63 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32115.75 | 1496.44 | 1620.7198 | 124.2798 | 171.56 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32165.76 | 1495.39 | 1620.6535 | 125.2635 | 172.61 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32215.78 | 1494.14 | 1620.5872 | 126.4472 | 173.86 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32265.78 | 1494.04 | 1620.5209 | 126.4809 | 173.96 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32315.79 | 1492.88 | 1620.4546 | 127.5746 | 175.12 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32365.79 | 1492.61 | 1620.3883 | 127.7783 | 175.39 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32415.82 | 1490.9 | 1620.322 | 129.422 | 177.1 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32465.85 | 1489.13 | 1620.2556 | 131.1256 | 178.87 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32515.86 | 1488.55 | 1620.1893 | 131.6393 | 179.45 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32565.86 | 1487.87 | 1620.123 | 132.253 | 180.13 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32615.86 | 1488.46 | 1620.0567 | 131.5967 | 179.54 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32665.87 | 1487.6 | 1619.9904 | 132.3904 | 180.4 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32715.87 | 1486.97 | 1619.9241 | 132.9541 | 181.03 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32765.9 | 1485.36 | 1619.8578 | 134.4978 | 182.64 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32815.91 | 1484.45 | 1619.7915 | 135.3415 | 183.55 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32865.92 | 1483.53 | 1619.7252 | 136.1952 | 184.47 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32915.92 | 1483.62 | 1619.6589 | 136.0389 | 184.38 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 32965.94 | 1482.25 | 1619.5926 | 137.3426 | 185.75 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33015.98 | 1480.17 | 1619.5262 | 139.3562 | 187.83 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33065.99 | 1481.16 | 1619.4599 | 138.2999 | 186.84 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33116.01 | 1479.62 | 1619.3936 | 139.7736 | 188.38 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33166.02 | 1479.18 | 1619.3273 | 140.1473 | 188.82 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33216.02 | 1478.95 | 1619.261 | 140.311 | 189.05 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33266.02 | 1478.42 | 1619.1947 | 140.7747 | 189.58 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33316.02 | 1478.14 | 1619.1284 | 140.9884 | 189.86 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33366.03 | 1477.07 | 1619.0621 | 141.9921 | 190.93 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33416.03 | 1477.49 | 1618.9958 | 141.5058 | 190.51 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33466.03 | 1477.91 | 1618.9295 | 141.0195 | 190.09 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33516.05 | 1476.73 | 1618.8632 | 142.1332 | 191.27 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33566.09 | 1478.71 | 1618.7969 | 140.0869 | 189.29 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33616.16 | 1481.42 | 1618.7305 | 137.3105 | 186.58 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33666.19 | 1483.1 | 1618.6642 | 135.5642 | 184.9 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33716.31 | 1486.62 | 1618.5977 | 131.9777 | 181.38 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33766.32 | 1487.47 | 1618.5314 | 131.0614 | 180.53 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33816.41 | 1490.41 | 1618.465 | 128.055 | 177.59 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33866.5 | 1493.5 | 1618.3986 | 124.8986 | 174.5 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33916.51 | 1494.21 | 1618.3323 | 124.1223 | 173.79 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 33966.54 | 1496.11 | 1618.266 | 122.156 | 171.89 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34016.56 | 1497.4 | 1618.1996 | 120.7996 | 170.6 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34066.58 | 1498.92 | 1618.1333 | 119.2133 | 169.08 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34116.59 | 1499.77 | 1618.067 | 118.297 | 168.23 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34166.59 | 1500.26 | 1618.0007 | 117.7407 | 167.74 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34216.6 | 1501.39 | 1617.9344 | 116.5444 | 166.61 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34266.61 | 1501.82 | 1617.8681 | 116.0481 | 166.18 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34316.61 | 1501.91 | 1617.8018 | 115.8918 | 166.09 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34366.61 | 1501.99 | 1617.7355 | 115.7455 | 166.01 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34416.61 | 1502.78 | 1617.6692 | 114.8892 | 165.22 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34466.61 | 1502.45 | 1617.6029 | 115.1529 | 165.55 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34516.62 | 1503.43 | 1617.5366 | 114.1066 | 164.57 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34566.64 | 1504.79 | 1617.4703 | 112.6803 | 163.21 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34616.64 | 1504.57 | 1617.404 | 112.834 | 163.43 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34666.67 | 1506.15 | 1617.3377 | 111.1877 | 161.85 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34716.69 | 1507.6 | 1617.2714 | 109.6714 | 160.4 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34766.69 | 1507.37 | 1617.2051 | 109.8351 | 160.63 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34816.7 | 1508.51 | 1617.1388 | 108.6288 | 159.49 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34866.7 | 1509.02 | 1617.0725 | 108.0525 | 158.98 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34916.71 | 1509.43 | 1617.0062 | 107.5762 | 158.57 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 34966.71 | 1509.19 | 1616.9399 | 107.7499 | 158.81 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35016.71 | 1508.85 | 1616.8736 | 108.0236 | 159.15 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35066.72 | 1507.99 | 1616.8073 | 108.8173 | 160.01 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35116.72 | 1507.6 | 1616.741 | 109.141 | 160.4 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35166.73 | 1506.64 | 1616.6747 | 110.0347 | 161.36 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35216.74 | 1505.66 | 1616.6084 | 110.9484 | 162.34 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35266.75 | 1504.64 | 1616.5421 | 111.9021 | 163.36 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35316.75 | 1504.45 | 1616.4758 | 112.0258 | 163.55 | 25 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35366.75 | 1504.92 | 1616.4095 | 111.4895 | 163.08 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35416.77 | 1506.26 | 1616.3432 | 110.0832 | 161.74 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35466.82 | 1508.51 | 1616.2768 | 107.7668 | 159.49 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35516.83 | 1509.38 | 1616.2105 | 106.8305 | 158.62 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35566.85 | 1511.07 | 1616.1442 | 105.0742 | 156.93 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35616.89 | 1513.09 | 1616.0779 | 102.9879 | 154.91 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35666.92 | 1514.63 | 1616.0115 | 101.3815 | 153.37 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35716.93 | 1515.9 | 1615.9452 | 100.0452 | 152.1 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35766.95 | 1517.28 | 1615.8789 | 98.5989 | 150.72 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35816.96 | 1517.8 | 1615.8126 | 98.0126 | 150.2 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35866.95 | 1518.65 | 1615.7463 | 97.0963 | 149.35 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35916.96 | 1519.36 | 1615.68 | 96.32 | 148.64 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 35966.96 | 1519.46 | 1615.6137 | 96.1537 | 148.54 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36016.96 | 1519.49 | 1615.5474 | 96.0574 | 148.51 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36066.96 | 1519.81 | 1615.4811 | 95.6711 | 148.19 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36116.96 | 1520.15 | 1615.4148 | 95.2648 | 147.85 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36166.97 | 1521.02 | 1615.3485 | 94.3285 | 146.98 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36216.99 | 1522.36 | 1615.2822 | 92.9222 | 145.64 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36266.99 | 1523.3 | 1615.2159 | 91.9159 | 144.7 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36317.32 | 1528.99 | 1615.1492 | 86.1592 | 139.01 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36367.32 | 1529.08 | 1615.0829 | 86.0029 | 138.92 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36417.73 | 1535.48 | 1615.0161 | 79.5361 | 132.52 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36467.73 | 1535.45 | 1614.9498 | 79.4998 | 132.55 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36517.94 | 1540.05 | 1614.8832 | 74.8332 | 127.95 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36568.01 | 1542.8 | 1614.8168 | 72.0168 | 125.2 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36618.07 | 1545.28 | 1614.7505 | 69.4705 | 122.72 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36668.07 | 1545.57 | 1614.6842 | 69.1142 | 122.43 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36718.07 | 1545.74 | 1614.6179 | 68.8779 | 122.26 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36768.08 | 1545.89 | 1614.5516 | 68.6616 | 122.11 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36818.08 | 1545.94 | 1614.4853 | 68.5453 | 122.06 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36868.08 | 1546.7 | 1614.419 | 67.719 | 121.3 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36918.08 | 1546.42 | 1614.3527 | 67.9327 | 121.58 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 36968.08 | 1546.06 | 1614.2864 | 68.2264 | 121.94 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37018.09 | 1546.67 | 1614.2201 | 67.5501 | 121.33 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37068.09 | 1547.11 | 1614.1538 | 67.0438 | 120.89 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37118.09 | 1546.79 | 1614.0875 | 67.2975 | 121.21 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37168.09 | 1546.07 | 1614.0212 | 67.9512 | 121.93 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37218.09 | 1546.04 | 1613.9549 | 67.9149 | 121.96 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37268.14 | 1543.91 | 1613.8886 | 69.9786 | 124.09 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37318.16 | 1542.48 | 1613.8223 | 71.3423 | 125.52 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37368.18 | 1543.8 | 1613.7559 | 69.9559 | 124.2 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37418.19 | 1544.87 | 1613.6896 | 68.8196 | 123.13 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37468.19 | 1544.82 | 1613.6233 | 68.8033 | 123.18 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37518.19 | 1544.58 | 1613.557 | 68.977 | 123.42 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37568.19 | 1544.32 | 1613.4908 | 69.1708 | 123.68 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37618.19 | 1544.41 | 1613.4245 | 69.0145 | 123.59 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37668.2 | 1543.64 | 1613.3582 | 69.7182 | 124.36 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37718.2 | 1543.92 | 1613.2919 | 69.3719 | 124.08 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37768.22 | 1542.4 | 1613.2255 | 70.8255 | 125.6 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37818.28 | 1539.99 | 1613.1592 | 73.1692 | 128.01 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37868.3 | 1538.42 | 1613.0929 | 74.6729 | 129.58 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37918.3 | 1538.51 | 1613.0266 | 74.5166 | 129.49 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 37968.39 | 1535.53 | 1612.9602 | 77.4302 | 132.47 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38018.43 | 1533.6 | 1612.8938 | 79.2938 | 134.4 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38068.43 | 1533.07 | 1612.8275 | 79.7575 | 134.93 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38118.44 | 1532.25 | 1612.7612 | 80.5112 | 135.75 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38168.44 | 1532.72 | 1612.6949 | 79.9749 | 135.28 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38218.45 | 1533.57 | 1612.6286 | 79.0586 | 134.43 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38268.48 | 1535.45 | 1612.5623 | 77.1123 | 132.55 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38318.49 | 1536.2 | 1612.496 | 76.296 | 131.8 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38368.5 | 1537.79 | 1612.4297 | 74.6397 | 130.21 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38418.52 | 1538.94 | 1612.3634 | 73.4234 | 129.06 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38468.53 | 1540.08 | 1612.2971 | 72.2171 | 127.92 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38518.54 | 1541.06 | 1612.2307 | 71.1707 | 126.94 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38568.59 | 1543.2 | 1612.1644 | 68.9644 | 124.8 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38618.6 | 1544.22 | 1612.0981 | 67.8781 | 123.78 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38668.65 | 1546.42 | 1612.0317 | 65.6117 | 121.58 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38718.65 | 1545.89 | 1611.9654 | 66.0754 | 122.11 | 16 | 25
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | 38930.17 | 1554.3 | 1611.685 | 57.385 | 113.7 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 0 | 1554.3 | 1738.2284 | 183.9284 | 183.9284 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 153.17 | 1560.44 | 1737.9898 | 177.5498 | 177.5498 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 173.18 | 1560.88 | 1737.9587 | 177.0787 | 177.0787 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 193.2 | 1561.81 | 1737.9275 | 176.1175 | 176.1175 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 213.21 | 1562.48 | 1737.8963 | 175.4163 | 175.4163 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 233.23 | 1563.35 | 1737.8651 | 174.5151 | 174.5151 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 253.24 | 1564.17 | 1737.834 | 173.664 | 173.664 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 273.25 | 1564.58 | 1737.8028 | 173.2228 | 173.2228 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 293.26 | 1565.19 | 1737.7716 | 172.5816 | 172.5816 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 313.26 | 1565.34 | 1737.7405 | 172.4005 | 172.4005 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 333.27 | 1566 | 1737.7093 | 171.7093 | 171.7093 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 353.28 | 1566.57 | 1737.6781 | 171.1081 | 171.1081 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 373.29 | 1567.26 | 1737.647 | 170.387 | 170.387 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 393.32 | 1568.41 | 1737.6158 | 169.2058 | 169.2058 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 413.32 | 1568.24 | 1737.5846 | 169.3446 | 169.3446 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 433.34 | 1569.08 | 1737.5534 | 168.4734 | 168.4734 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 453.36 | 1569.91 | 1737.5223 | 167.6123 | 167.6123 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 473.36 | 1569.63 | 1737.4911 | 167.8611 | 167.8611 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 493.37 | 1570.39 | 1737.4599 | 167.0699 | 167.0699 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 513.39 | 1571.14 | 1737.4287 | 166.2887 | 166.2887 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 533.41 | 1572.05 | 1737.3976 | 165.3476 | 165.3476 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 553.41 | 1572.05 | 1737.3664 | 165.3164 | 165.3164 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 573.44 | 1573.18 | 1737.3352 | 164.1552 | 164.1552 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 593.45 | 1573.81 | 1737.304 | 163.494 | 163.494 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 613.48 | 1574.88 | 1737.2728 | 162.3928 | 162.3928 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 633.48 | 1574.88 | 1737.2417 | 162.3617 | 162.3617 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 653.52 | 1576.12 | 1737.2105 | 161.0905 | 161.0905 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 673.52 | 1576.58 | 1737.1793 | 160.5993 | 160.5993 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 693.54 | 1577.31 | 1737.1481 | 159.8381 | 159.8381 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 713.54 | 1577.31 | 1737.117 | 159.807 | 159.807 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 733.56 | 1578.29 | 1737.0858 | 158.7958 | 158.7958 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 753.56 | 1578.62 | 1737.0546 | 158.4346 | 158.4346 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 773.58 | 1579.5 | 1737.0235 | 157.5235 | 157.5235 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 793.59 | 1580.2 | 1736.9923 | 156.7923 | 156.7923 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 813.6 | 1580.33 | 1736.9611 | 156.6311 | 156.6311 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 833.6 | 1580.52 | 1736.93 | 156.41 | 156.41 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 853.6 | 1580.56 | 1736.8988 | 156.3388 | 156.3388 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 873.6 | 1580.94 | 1736.8677 | 155.9277 | 155.9277 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 893.6 | 1580.83 | 1736.8365 | 156.0065 | 156.0065 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 913.6 | 1580.85 | 1736.8054 | 155.9554 | 155.9554 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 933.6 | 1580.62 | 1736.7742 | 156.1542 | 156.1542 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 953.6 | 1580.48 | 1736.743 | 156.263 | 156.263 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 973.6 | 1580.45 | 1736.7119 | 156.2619 | 156.2619 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 993.6 | 1580.36 | 1736.6807 | 156.3207 | 156.3207 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1013.6 | 1580.16 | 1736.6496 | 156.4896 | 156.4896 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1033.6 | 1579.91 | 1736.6184 | 156.7084 | 156.7084 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1053.61 | 1579.76 | 1736.5873 | 156.8273 | 156.8273 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1073.61 | 1579.64 | 1736.5561 | 156.9161 | 156.9161 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1093.61 | 1579.83 | 1736.525 | 156.695 | 156.695 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1112.79 | 1579.91 | 1736.4951 | 156.5851 | 156.5851 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1132.79 | 1579.53 | 1736.4639 | 156.9339 | 156.9339 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1152.79 | 1579.21 | 1736.4328 | 157.2228 | 157.2228 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1172.79 | 1578.94 | 1736.4016 | 157.4616 | 157.4616 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1192.8 | 1578.76 | 1736.3705 | 157.6105 | 157.6105 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1212.8 | 1578.5 | 1736.3393 | 157.8393 | 157.8393 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1232.81 | 1577.81 | 1736.3081 | 158.4981 | 158.4981 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1252.81 | 1577.67 | 1736.277 | 158.607 | 158.607 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1272.81 | 1577.48 | 1736.2458 | 158.7658 | 158.7658 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1292.82 | 1576.9 | 1736.2147 | 159.3147 | 159.3147 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1312.82 | 1576.66 | 1736.1835 | 159.5235 | 159.5235 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1332.83 | 1576.11 | 1736.1523 | 160.0423 | 160.0423 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1352.83 | 1575.81 | 1736.1212 | 160.3112 | 160.3112 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1372.83 | 1575.51 | 1736.09 | 160.58 | 160.58 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1392.84 | 1575.19 | 1736.0589 | 160.8689 | 160.8689 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1412.84 | 1574.82 | 1736.0277 | 161.2077 | 161.2077 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1432.85 | 1574.26 | 1735.9965 | 161.7365 | 161.7365 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1452.85 | 1573.99 | 1735.9654 | 161.9754 | 161.9754 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1472.85 | 1573.61 | 1735.9342 | 162.3242 | 162.3242 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1492.86 | 1573.06 | 1735.9031 | 162.8431 | 162.8431 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1512.86 | 1572.79 | 1735.8719 | 163.0819 | 163.0819 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1532.87 | 1572.12 | 1735.8407 | 163.7207 | 163.7207 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1552.87 | 1571.87 | 1735.8096 | 163.9396 | 163.9396 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1572.89 | 1571.16 | 1735.7784 | 164.6184 | 164.6184 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1592.9 | 1570.46 | 1735.7472 | 165.2872 | 165.2872 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1612.91 | 1569.86 | 1735.7161 | 165.8561 | 165.8561 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1632.92 | 1569.09 | 1735.6849 | 166.5949 | 166.5949 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1652.93 | 1568.6 | 1735.6537 | 167.0537 | 167.0537 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1672.96 | 1567.44 | 1735.6225 | 168.1825 | 168.1825 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1692.96 | 1567.44 | 1735.5914 | 168.1514 | 168.1514 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1712.99 | 1566.3 | 1735.5602 | 169.2602 | 169.2602 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1733.03 | 1565.07 | 1735.529 | 170.459 | 170.459 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1753.05 | 1564.14 | 1735.4978 | 171.3578 | 171.3578 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1773.05 | 1564.14 | 1735.4666 | 171.3266 | 171.3266 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1793.08 | 1563.17 | 1735.4354 | 172.2654 | 172.2654 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1813.13 | 1561.75 | 1735.4042 | 173.6542 | 173.6542 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1833.13 | 1561.93 | 1735.373 | 173.443 | 173.443 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1853.13 | 1561.71 | 1735.3419 | 173.6319 | 173.6319 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1873.13 | 1561.68 | 1735.3107 | 173.6307 | 173.6307 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1893.13 | 1561.63 | 1735.2796 | 173.6496 | 173.6496 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1913.14 | 1562.09 | 1735.2484 | 173.1584 | 173.1584 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1933.14 | 1561.89 | 1735.2173 | 173.3273 | 173.3273 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1953.14 | 1561.93 | 1735.1861 | 173.2561 | 173.2561 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1973.15 | 1562.62 | 1735.1549 | 172.5349 | 172.5349 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 1993.15 | 1562.64 | 1735.1238 | 172.4838 | 172.4838 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2013.18 | 1563.79 | 1735.0926 | 171.3026 | 171.3026 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2033.23 | 1565.13 | 1735.0613 | 169.9313 | 169.9313 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2053.23 | 1565.13 | 1735.0302 | 169.9002 | 169.9002 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2073.29 | 1566.71 | 1734.9989 | 168.2889 | 168.2889 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2093.3 | 1567.39 | 1734.9678 | 167.5778 | 167.5778 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2113.3 | 1567.39 | 1734.9366 | 167.5466 | 167.5466 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2133.32 | 1568.35 | 1734.9054 | 166.5554 | 166.5554 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2153.34 | 1569.14 | 1734.8743 | 165.7343 | 165.7343 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2173.34 | 1568.81 | 1734.8431 | 166.0331 | 166.0331 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2193.36 | 1569.56 | 1734.8119 | 165.2519 | 165.2519 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2213.38 | 1570.45 | 1734.7807 | 164.3307 | 164.3307 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2233.38 | 1570.45 | 1734.7496 | 164.2996 | 164.2996 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2253.38 | 1570.68 | 1734.7184 | 164.0384 | 164.0384 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2273.38 | 1571.04 | 1734.6873 | 163.6473 | 163.6473 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2293.38 | 1571.21 | 1734.6561 | 163.4461 | 163.4461 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2313.38 | 1571.47 | 1734.625 | 163.155 | 163.155 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2333.38 | 1571.25 | 1734.5938 | 163.3438 | 163.3438 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2353.38 | 1571.25 | 1734.5627 | 163.3127 | 163.3127 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2373.38 | 1571.21 | 1734.5315 | 163.3215 | 163.3215 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2393.38 | 1571.21 | 1734.5004 | 163.2904 | 163.2904 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2413.38 | 1571.29 | 1734.4692 | 163.1792 | 163.1792 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2433.38 | 1571.09 | 1734.438 | 163.348 | 163.348 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2453.38 | 1571.09 | 1734.4069 | 163.3169 | 163.3169 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2473.39 | 1570.83 | 1734.3757 | 163.5457 | 163.5457 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2493.39 | 1570.92 | 1734.3446 | 163.4246 | 163.4246 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2513.39 | 1570.92 | 1734.3134 | 163.3934 | 163.3934 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2533.39 | 1571.02 | 1734.2823 | 163.2623 | 163.2623 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2553.39 | 1571.57 | 1734.2511 | 162.6811 | 162.6811 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2573.39 | 1571.57 | 1734.22 | 162.65 | 162.65 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2593.4 | 1571.98 | 1734.1888 | 162.2088 | 162.2088 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2613.4 | 1572.24 | 1734.1576 | 161.9176 | 161.9176 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2633.41 | 1572.86 | 1734.1265 | 161.2665 | 161.2665 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2653.41 | 1572.86 | 1734.0953 | 161.2353 | 161.2353 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2673.41 | 1573.28 | 1734.0642 | 160.7842 | 160.7842 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2693.42 | 1573.56 | 1734.033 | 160.473 | 160.473 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2713.42 | 1573.56 | 1734.0018 | 160.4418 | 160.4418 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2733.43 | 1574.22 | 1733.9707 | 159.7507 | 159.7507 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2753.43 | 1574.63 | 1733.9395 | 159.3095 | 159.3095 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2773.43 | 1574.63 | 1733.9084 | 159.2784 | 159.2784 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2793.43 | 1574.56 | 1733.8772 | 159.3172 | 159.3172 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2813.43 | 1574.68 | 1733.8461 | 159.1661 | 159.1661 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2833.43 | 1574.99 | 1733.8149 | 158.8249 | 158.8249 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2853.44 | 1574.35 | 1733.7837 | 159.4337 | 159.4337 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2873.45 | 1574.59 | 1733.7526 | 159.1626 | 159.1626 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2893.45 | 1574.48 | 1733.7214 | 159.2414 | 159.2414 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2913.45 | 1574.19 | 1733.6903 | 159.5003 | 159.5003 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2933.45 | 1574.19 | 1733.6591 | 159.4691 | 159.4691 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2953.45 | 1574.09 | 1733.6279 | 159.5379 | 159.5379 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2973.45 | 1573.86 | 1733.5968 | 159.7368 | 159.7368 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 2993.45 | 1574.19 | 1733.5656 | 159.3756 | 159.3756 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3013.45 | 1574.42 | 1733.5345 | 159.1145 | 159.1145 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3033.45 | 1574.5 | 1733.5033 | 159.0033 | 159.0033 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3053.45 | 1574.57 | 1733.4722 | 158.9022 | 158.9022 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3073.47 | 1575.25 | 1733.441 | 158.191 | 158.191 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3093.5 | 1576.47 | 1733.4098 | 156.9398 | 156.9398 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3113.5 | 1576.47 | 1733.3786 | 156.9086 | 156.9086 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3133.59 | 1578.34 | 1733.3474 | 155.0074 | 155.0074 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3153.64 | 1579.81 | 1733.3161 | 153.5061 | 153.5061 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3173.65 | 1580.02 | 1733.285 | 153.265 | 153.265 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3193.69 | 1581.29 | 1733.2537 | 151.9637 | 151.9637 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3213.73 | 1582.56 | 1733.2225 | 150.6625 | 150.6625 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3233.74 | 1583.32 | 1733.1914 | 149.8714 | 149.8714 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3253.77 | 1584.45 | 1733.1602 | 148.7102 | 148.7102 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3273.77 | 1584.45 | 1733.129 | 148.679 | 148.679 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3293.79 | 1585.3 | 1733.0978 | 147.7978 | 147.7978 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3313.79 | 1585.3 | 1733.0667 | 147.7667 | 147.7667 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3333.8 | 1586 | 1733.0355 | 147.0355 | 147.0355 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3353.8 | 1586.28 | 1733.0043 | 146.7243 | 146.7243 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3373.81 | 1586.7 | 1732.9732 | 146.2732 | 146.2732 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3393.81 | 1586.7 | 1732.942 | 146.242 | 146.242 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3413.81 | 1587.05 | 1732.9109 | 145.8609 | 145.8609 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3433.81 | 1587.05 | 1732.8797 | 145.8297 | 145.8297 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3453.81 | 1586.96 | 1732.8486 | 145.8886 | 145.8886 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3473.81 | 1586.82 | 1732.8174 | 145.9974 | 145.9974 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3493.81 | 1587.07 | 1732.7863 | 145.7163 | 145.7163 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3513.83 | 1587.91 | 1732.7551 | 144.8451 | 144.8451 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3533.84 | 1587.32 | 1732.7239 | 145.4039 | 145.4039 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3553.84 | 1586.92 | 1732.6927 | 145.7727 | 145.7727 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3573.86 | 1587.67 | 1732.6616 | 144.9916 | 144.9916 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3593.86 | 1587.61 | 1732.6304 | 145.0204 | 145.0204 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3613.86 | 1587.35 | 1732.5993 | 145.2493 | 145.2493 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3633.89 | 1588.45 | 1732.5681 | 144.1181 | 144.1181 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3653.9 | 1587.87 | 1732.5369 | 144.6669 | 144.6669 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3673.91 | 1587.21 | 1732.5057 | 145.2957 | 145.2957 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3693.95 | 1588.55 | 1732.4745 | 143.9245 | 143.9245 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3713.98 | 1587.45 | 1732.4433 | 144.9933 | 144.9933 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3734 | 1588.17 | 1732.4121 | 144.2421 | 144.2421 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3754 | 1588.18 | 1732.381 | 144.201 | 144.201 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3774 | 1588.17 | 1732.3498 | 144.1798 | 144.1798 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3794 | 1588.52 | 1732.3187 | 143.7987 | 143.7987 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3814.01 | 1588.1 | 1732.2875 | 144.1875 | 144.1875 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3834.03 | 1589.02 | 1732.2563 | 143.2363 | 143.2363 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3854.04 | 1588.38 | 1732.2251 | 143.8451 | 143.8451 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3874.04 | 1588.26 | 1732.194 | 143.934 | 143.934 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3894.04 | 1588.05 | 1732.1628 | 144.1128 | 144.1128 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3914.06 | 1587.09 | 1732.1316 | 145.0416 | 145.0416 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3934.06 | 1587.12 | 1732.1005 | 144.9805 | 144.9805 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3954.08 | 1586.16 | 1732.0693 | 145.9093 | 145.9093 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3974.08 | 1586.09 | 1732.0382 | 145.9482 | 145.9482 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 3994.1 | 1585.26 | 1732.007 | 146.747 | 146.747 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4014.14 | 1584.04 | 1731.9758 | 147.9358 | 147.9358 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4034.25 | 1581.94 | 1731.9444 | 150.0044 | 150.0044 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4054.29 | 1583.18 | 1731.9132 | 148.7332 | 148.7332 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4074.34 | 1584.59 | 1731.882 | 147.292 | 147.292 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4094.35 | 1585.34 | 1731.8508 | 146.5108 | 146.5108 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4114.35 | 1585.1 | 1731.8197 | 146.7197 | 146.7197 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4134.39 | 1586.26 | 1731.7884 | 145.5284 | 145.5284 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4154.41 | 1587.17 | 1731.7573 | 144.5873 | 144.5873 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4174.41 | 1587.14 | 1731.7261 | 144.5861 | 144.5861 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4194.43 | 1588.06 | 1731.6949 | 143.6349 | 143.6349 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4214.45 | 1589.04 | 1731.6637 | 142.6237 | 142.6237 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4234.45 | 1588.72 | 1731.6326 | 142.9126 | 142.9126 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4254.46 | 1589.1 | 1731.6014 | 142.5014 | 142.5014 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4274.47 | 1589.68 | 1731.5702 | 141.8902 | 141.8902 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4294.47 | 1589.3 | 1731.5391 | 142.2391 | 142.2391 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4314.47 | 1589.03 | 1731.5079 | 142.4779 | 142.4779 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4334.48 | 1589.47 | 1731.4768 | 142.0068 | 142.0068 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4354.48 | 1589.25 | 1731.4456 | 142.1956 | 142.1956 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4374.48 | 1589.03 | 1731.4145 | 142.3845 | 142.3845 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4394.49 | 1588.45 | 1731.3833 | 142.9333 | 142.9333 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4414.49 | 1587.95 | 1731.3521 | 143.4021 | 143.4021 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4434.5 | 1588.45 | 1731.321 | 142.871 | 142.871 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4454.52 | 1587.47 | 1731.2898 | 143.8198 | 143.8198 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4474.53 | 1587.04 | 1731.2586 | 144.2186 | 144.2186 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4494.53 | 1586.94 | 1731.2275 | 144.2875 | 144.2875 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4514.6 | 1585.26 | 1731.1962 | 145.9362 | 145.9362 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4534.61 | 1585.86 | 1731.165 | 145.305 | 145.305 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4554.61 | 1585.88 | 1731.1339 | 145.2539 | 145.2539 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4574.64 | 1584.69 | 1731.1027 | 146.4127 | 146.4127 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4594.64 | 1584.72 | 1731.0715 | 146.3515 | 146.3515 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4614.67 | 1583.69 | 1731.0403 | 147.3503 | 147.3503 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4634.7 | 1582.56 | 1731.0091 | 148.4491 | 148.4491 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4654.71 | 1582.16 | 1730.978 | 148.818 | 148.818 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4674.72 | 1581.51 | 1730.9468 | 149.4368 | 149.4368 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4694.72 | 1581.09 | 1730.9156 | 149.8256 | 149.8256 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4714.79 | 1579.41 | 1730.8844 | 151.4744 | 151.4744 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4734.8 | 1578.8 | 1730.8532 | 152.0532 | 152.0532 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4754.84 | 1577.55 | 1730.822 | 153.272 | 153.272 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4774.88 | 1576.27 | 1730.7908 | 154.5208 | 154.5208 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4794.88 | 1575.92 | 1730.7596 | 154.8396 | 154.8396 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4814.97 | 1574.11 | 1730.7283 | 156.6183 | 156.6183 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4835.01 | 1575.5 | 1730.6971 | 155.1971 | 155.1971 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4855.01 | 1575.4 | 1730.666 | 155.266 | 155.266 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4875.04 | 1576.46 | 1730.6348 | 154.1748 | 154.1748 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4895.06 | 1577.4 | 1730.6036 | 153.2036 | 153.2036 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4915.06 | 1577.28 | 1730.5724 | 153.2924 | 153.2924 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4935.09 | 1578.29 | 1730.5412 | 152.2512 | 152.2512 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4955.13 | 1577.03 | 1730.51 | 153.48 | 153.48 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4975.14 | 1577.68 | 1730.4788 | 152.7988 | 152.7988 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 4995.15 | 1578.14 | 1730.4477 | 152.3077 | 152.3077 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5015.15 | 1577.74 | 1730.4165 | 152.6765 | 152.6765 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5035.16 | 1578.48 | 1730.3853 | 151.9053 | 151.9053 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5055.19 | 1577.52 | 1730.3541 | 152.8341 | 152.8341 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5075.2 | 1578.27 | 1730.323 | 152.053 | 152.053 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5095.21 | 1577.65 | 1730.2918 | 152.6418 | 152.6418 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5115.22 | 1578.38 | 1730.2606 | 151.8806 | 151.8806 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5135.25 | 1577.3 | 1730.2294 | 152.9294 | 152.9294 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5155.25 | 1577.13 | 1730.1983 | 153.0683 | 153.0683 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5175.26 | 1576.67 | 1730.1671 | 153.4971 | 153.4971 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5195.26 | 1576.17 | 1730.136 | 153.966 | 153.966 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5215.27 | 1575.81 | 1730.1048 | 154.2948 | 154.2948 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5235.27 | 1575.29 | 1730.0736 | 154.7836 | 154.7836 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5255.28 | 1575.04 | 1730.0425 | 155.0025 | 155.0025 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5275.28 | 1574.65 | 1730.0113 | 155.3613 | 155.3613 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5295.28 | 1574.5 | 1729.9802 | 155.4802 | 155.4802 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5315.28 | 1574.34 | 1729.949 | 155.609 | 155.609 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5335.3 | 1573.57 | 1729.9178 | 156.3478 | 156.3478 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5355.3 | 1573.05 | 1729.8867 | 156.8367 | 156.8367 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5375.31 | 1572.39 | 1729.8555 | 157.4655 | 157.4655 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5395.33 | 1571.6 | 1729.8243 | 158.2243 | 158.2243 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5415.36 | 1570.55 | 1729.7931 | 159.2431 | 159.2431 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5435.36 | 1570.6 | 1729.762 | 159.162 | 159.162 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5455.43 | 1568.94 | 1729.7307 | 160.7907 | 160.7907 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5475.43 | 1568.45 | 1729.6995 | 161.2495 | 161.2495 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5495.47 | 1567.21 | 1729.6683 | 162.4583 | 162.4583 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5515.49 | 1566.37 | 1729.6371 | 163.2671 | 163.2671 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5535.52 | 1565.24 | 1729.6059 | 164.3659 | 164.3659 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5555.57 | 1563.87 | 1729.5747 | 165.7047 | 165.7047 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5575.61 | 1562.53 | 1729.5435 | 167.0135 | 167.0135 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5595.67 | 1560.95 | 1729.5123 | 168.5623 | 168.5623 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5615.67 | 1560.94 | 1729.4811 | 168.5411 | 168.5411 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5635.68 | 1560.37 | 1729.4499 | 169.0799 | 169.0799 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5655.88 | 1563.18 | 1729.4185 | 166.2385 | 166.2385 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5675.89 | 1563.96 | 1729.3873 | 165.4273 | 165.4273 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5695.91 | 1564.67 | 1729.3561 | 164.6861 | 164.6861 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5715.91 | 1564.44 | 1729.325 | 164.885 | 164.885 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5735.91 | 1564.23 | 1729.2938 | 165.0638 | 165.0638 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5755.91 | 1564.68 | 1729.2627 | 164.5827 | 164.5827 | 25 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5776.05 | 1567.04 | 1729.2313 | 162.1913 | 162.1913 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5796.05 | 1566.81 | 1729.2001 | 162.3901 | 162.3901 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5816.07 | 1567.74 | 1729.1689 | 161.4289 | 161.4289 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5836.1 | 1568.66 | 1729.1377 | 160.4777 | 160.4777 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5856.1 | 1569.1 | 1729.1066 | 160.0066 | 160.0066 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5876.13 | 1570.12 | 1729.0754 | 158.9554 | 158.9554 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5896.16 | 1568.92 | 1729.0442 | 160.1242 | 160.1242 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5916.23 | 1570.53 | 1729.0129 | 158.4829 | 158.4829 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5936.23 | 1570.8 | 1728.9818 | 158.1818 | 158.1818 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5956.25 | 1571.76 | 1728.9506 | 157.1906 | 157.1906 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5976.26 | 1572.33 | 1728.9194 | 156.5894 | 156.5894 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 5996.27 | 1572.87 | 1728.8883 | 156.0183 | 156.0183 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6016.27 | 1572.7 | 1728.8571 | 156.1571 | 156.1571 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6036.27 | 1572.77 | 1728.8259 | 156.0559 | 156.0559 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6056.29 | 1573.67 | 1728.7948 | 155.1248 | 155.1248 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6076.39 | 1571.63 | 1728.7635 | 157.1335 | 157.1335 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6096.52 | 1573.85 | 1728.7321 | 154.8821 | 154.8821 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6116.53 | 1573.2 | 1728.7009 | 155.5009 | 155.5009 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6136.6 | 1574.9 | 1728.6697 | 153.7697 | 153.7697 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6156.6 | 1574.86 | 1728.6385 | 153.7785 | 153.7785 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6176.6 | 1575 | 1728.6074 | 153.6074 | 153.6074 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6196.6 | 1574.81 | 1728.5762 | 153.7662 | 153.7662 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6216.65 | 1576.16 | 1728.545 | 152.385 | 152.385 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6236.76 | 1574.04 | 1728.5137 | 154.4737 | 154.4737 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6256.76 | 1574.24 | 1728.4825 | 154.2425 | 154.2425 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6276.78 | 1573.36 | 1728.4513 | 155.0913 | 155.0913 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6296.79 | 1574.06 | 1728.4201 | 154.3601 | 154.3601 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6316.83 | 1575.28 | 1728.3889 | 153.1089 | 153.1089 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6336.85 | 1576.26 | 1728.3577 | 152.0977 | 152.0977 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6356.92 | 1577.92 | 1728.3265 | 150.4065 | 150.4065 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6376.95 | 1578.95 | 1728.2953 | 149.3453 | 149.3453 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6396.97 | 1579.96 | 1728.2641 | 148.3041 | 148.3041 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6416.98 | 1579.47 | 1728.2329 | 148.7629 | 148.7629 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6436.98 | 1579.6 | 1728.2018 | 148.6018 | 148.6018 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6456.98 | 1579.42 | 1728.1706 | 148.7506 | 148.7506 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6476.98 | 1579.35 | 1728.1395 | 148.7895 | 148.7895 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6497 | 1580.18 | 1728.1083 | 147.9283 | 147.9283 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6517.08 | 1582.05 | 1728.077 | 146.027 | 146.027 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6537.11 | 1583.07 | 1728.0458 | 144.9758 | 144.9758 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6557.17 | 1584.65 | 1728.0146 | 143.3646 | 143.3646 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6577.24 | 1586.3 | 1727.9833 | 141.6833 | 141.6833 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6597.29 | 1587.65 | 1727.9521 | 140.3021 | 140.3021 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6617.41 | 1589.85 | 1727.9207 | 138.0707 | 138.0707 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6637.44 | 1591.04 | 1727.8895 | 136.8495 | 136.8495 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6657.47 | 1592.19 | 1727.8583 | 135.6683 | 135.6683 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6677.66 | 1594.95 | 1727.8269 | 132.8769 | 132.8769 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6697.72 | 1593.48 | 1727.7956 | 134.3156 | 134.3156 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6717.76 | 1594.73 | 1727.7644 | 133.0344 | 133.0344 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6737.76 | 1595.16 | 1727.7333 | 132.5733 | 132.5733 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6757.77 | 1595.84 | 1727.7021 | 131.8621 | 131.8621 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6777.79 | 1596.77 | 1727.6709 | 130.9009 | 130.9009 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6797.8 | 1597.1 | 1727.6397 | 130.5397 | 130.5397 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6817.81 | 1597.73 | 1727.6086 | 129.8786 | 129.8786 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6837.81 | 1598.12 | 1727.5774 | 129.4574 | 129.4574 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6857.82 | 1598.66 | 1727.5462 | 128.8862 | 128.8862 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6877.82 | 1599.06 | 1727.5151 | 128.4551 | 128.4551 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6898.06 | 1599.4 | 1727.4836 | 128.0836 | 128.0836 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6918.06 | 1599.05 | 1727.4524 | 128.4024 | 128.4024 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6938.06 | 1599.15 | 1727.4213 | 128.2713 | 128.2713 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6958.06 | 1599.19 | 1727.3901 | 128.2001 | 128.2001 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6978.06 | 1599.51 | 1727.359 | 127.849 | 127.849 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 6998.06 | 1599.5 | 1727.3278 | 127.8278 | 127.8278 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7017.3 | 1600.25 | 1727.2978 | 127.0478 | 127.0478 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7037.34 | 1601.6 | 1727.2666 | 125.6666 | 125.6666 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7057.34 | 1601.68 | 1727.2355 | 125.5555 | 125.5555 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7077.4 | 1603.2 | 1727.2042 | 124.0042 | 124.0042 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7097.41 | 1603.85 | 1727.173 | 123.323 | 123.323 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7117.42 | 1604.55 | 1727.1419 | 122.5919 | 122.5919 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7137.44 | 1605.42 | 1727.1107 | 121.6907 | 121.6907 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7157.45 | 1605.97 | 1727.0795 | 121.1095 | 121.1095 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7177.49 | 1607.25 | 1727.0483 | 119.7983 | 119.7983 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7197.5 | 1607.77 | 1727.0171 | 119.2471 | 119.2471 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7217.52 | 1608.77 | 1726.986 | 118.216 | 118.216 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7237.52 | 1609.13 | 1726.9548 | 117.8248 | 117.8248 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7257.54 | 1609.87 | 1726.9236 | 117.0536 | 117.0536 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7277.54 | 1610.19 | 1726.8925 | 116.7025 | 116.7025 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7297.56 | 1611.06 | 1726.8613 | 115.8013 | 115.8013 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7317.56 | 1610.97 | 1726.8301 | 115.8601 | 115.8601 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7337.56 | 1611.37 | 1726.799 | 115.429 | 115.429 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7357.6 | 1612.6 | 1726.7678 | 114.1678 | 114.1678 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7377.62 | 1613.4 | 1726.7366 | 113.3366 | 113.3366 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7397.86 | 1615.02 | 1726.705 | 111.685 | 111.685 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7417.86 | 1614.9 | 1726.6739 | 111.7739 | 111.7739 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7437.94 | 1616.67 | 1726.6426 | 109.9726 | 109.9726 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7458.04 | 1618.7 | 1726.6113 | 107.9113 | 107.9113 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7478.09 | 1620.09 | 1726.5801 | 106.4901 | 106.4901 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7498.14 | 1621.52 | 1726.5488 | 105.0288 | 105.0288 | 16 | 25
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7518.16 | 1622.25 | 1726.5177 | 104.2677 | 104.2677 | 16 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7538.2 | 1623.51 | 1726.4864 | 102.9764 | 102.9764 | 16 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7558.33 | 1625.8 | 1726.4551 | 100.6551 | 100.6551 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7578.36 | 1626.97 | 1726.4239 | 99.4539 | 99.4539 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7598.44 | 1628.72 | 1726.3926 | 97.6726 | 97.6726 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7618.55 | 1630.82 | 1726.3613 | 95.5413 | 95.5413 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7638.58 | 1632 | 1726.3301 | 94.3301 | 94.3301 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7658.63 | 1633.43 | 1726.2989 | 92.8689 | 92.8689 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7678.65 | 1634.31 | 1726.2677 | 91.9577 | 91.9577 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7698.71 | 1635.84 | 1726.2364 | 90.3964 | 90.3964 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7718.72 | 1636.41 | 1726.2053 | 89.7953 | 89.7953 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7738.75 | 1637.56 | 1726.1741 | 88.6141 | 88.6141 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7758.77 | 1638.39 | 1726.1429 | 87.7529 | 87.7529 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7778.79 | 1639.38 | 1726.1117 | 86.7317 | 86.7317 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7798.8 | 1639.64 | 1726.0805 | 86.4405 | 86.4405 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7818.82 | 1640.65 | 1726.0493 | 85.3993 | 85.3993 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7838.82 | 1640.65 | 1726.0182 | 85.3682 | 85.3682 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7858.84 | 1641.49 | 1725.987 | 84.497 | 84.497 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7878.85 | 1642.23 | 1725.9558 | 83.7258 | 83.7258 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7898.85 | 1642.24 | 1725.9247 | 83.6847 | 83.6847 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7918.86 | 1642.75 | 1725.8935 | 83.1435 | 83.1435 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7938.87 | 1643.3 | 1725.8623 | 82.5623 | 82.5623 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7958.87 | 1643.65 | 1725.8312 | 82.1812 | 82.1812 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7978.87 | 1643.86 | 1725.8 | 81.94 | 81.94 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 7998.87 | 1644.14 | 1725.7689 | 81.6289 | 81.6289 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8018.88 | 1644.79 | 1725.7377 | 80.9477 | 80.9477 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8038.88 | 1645.03 | 1725.7066 | 80.6766 | 80.6766 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8058.89 | 1645.68 | 1725.6754 | 79.9954 | 79.9954 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8078.9 | 1645.37 | 1725.6442 | 80.2742 | 80.2742 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8098.9 | 1645.8 | 1725.6131 | 79.8131 | 79.8131 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8118.91 | 1646.31 | 1725.5819 | 79.2719 | 79.2719 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8138.91 | 1646.65 | 1725.5507 | 78.9007 | 78.9007 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8158.92 | 1647.17 | 1725.5196 | 78.3496 | 78.3496 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8178.93 | 1647.89 | 1725.4884 | 77.5984 | 77.5984 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8198.93 | 1647.77 | 1725.4572 | 77.6872 | 77.6872 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8218.93 | 1648.02 | 1725.4261 | 77.4061 | 77.4061 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8238.94 | 1648.62 | 1725.3949 | 76.7749 | 76.7749 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8258.95 | 1649.06 | 1725.3638 | 76.3038 | 76.3038 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8278.95 | 1649.15 | 1725.3326 | 76.1826 | 76.1826 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8298.95 | 1649.55 | 1725.3015 | 75.7515 | 75.7515 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8318.95 | 1649.91 | 1725.2703 | 75.3603 | 75.3603 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8338.96 | 1650.4 | 1725.2391 | 74.8391 | 74.8391 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8358.96 | 1650.6 | 1725.208 | 74.608 | 74.608 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8378.96 | 1650.85 | 1725.1768 | 74.3268 | 74.3268 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8398.97 | 1651.34 | 1725.1457 | 73.8057 | 73.8057 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8418.97 | 1651.73 | 1725.1145 | 73.3845 | 73.3845 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8439.03 | 1652.57 | 1725.0833 | 72.5133 | 72.5133 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8459.08 | 1653.93 | 1725.052 | 71.122 | 71.122 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8479.08 | 1654.07 | 1725.0209 | 70.9509 | 70.9509 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8499.09 | 1654.68 | 1724.9897 | 70.3097 | 70.3097 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8519.12 | 1655.88 | 1724.9585 | 69.0785 | 69.0785 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8539.14 | 1656.7 | 1724.9273 | 68.2273 | 68.2273 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8559.15 | 1657.31 | 1724.8961 | 67.5861 | 67.5861 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8579.15 | 1657.71 | 1724.865 | 67.155 | 67.155 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8599.15 | 1657.89 | 1724.8338 | 66.9438 | 66.9438 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8619.17 | 1658.68 | 1724.8027 | 66.1227 | 66.1227 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8639.18 | 1659.35 | 1724.7715 | 65.4215 | 65.4215 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8659.25 | 1660.97 | 1724.7402 | 63.7702 | 63.7702 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8679.25 | 1661.22 | 1724.7091 | 63.4891 | 63.4891 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8699.26 | 1662.07 | 1724.6779 | 62.6079 | 62.6079 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8719.29 | 1663.09 | 1724.6467 | 61.5567 | 61.5567 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8739.29 | 1663.41 | 1724.6155 | 61.2055 | 61.2055 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8759.32 | 1664.49 | 1724.5843 | 60.0943 | 60.0943 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8779.32 | 1664.76 | 1724.5532 | 59.7932 | 59.7932 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8799.34 | 1665.55 | 1724.522 | 58.972 | 58.972 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8819.37 | 1666.6 | 1724.4908 | 57.8908 | 57.8908 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8839.39 | 1667.45 | 1724.4596 | 57.0096 | 57.0096 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8859.41 | 1668.33 | 1724.4284 | 56.0984 | 56.0984 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8879.42 | 1669.12 | 1724.3973 | 55.2773 | 55.2773 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8899.43 | 1669.58 | 1724.3661 | 54.7861 | 54.7861 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8919.45 | 1670.49 | 1724.3349 | 53.8449 | 53.8449 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8939.47 | 1671.35 | 1724.3037 | 52.9537 | 52.9537 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8959.47 | 1671.75 | 1724.2726 | 52.5226 | 52.5226 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8979.49 | 1672.57 | 1724.2414 | 51.6714 | 51.6714 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 8999.51 | 1673.53 | 1724.2102 | 50.6802 | 50.6802 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9019.51 | 1673.89 | 1724.1791 | 50.2891 | 50.2891 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9039.52 | 1674.38 | 1724.1479 | 49.7679 | 49.7679 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9059.54 | 1675.31 | 1724.1167 | 48.8067 | 48.8067 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9079.56 | 1676.25 | 1724.0855 | 47.8355 | 47.8355 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9099.57 | 1676.61 | 1724.0544 | 47.4444 | 47.4444 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9119.59 | 1677.66 | 1724.0232 | 46.3632 | 46.3632 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9139.59 | 1677.94 | 1723.992 | 46.052 | 46.052 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9159.61 | 1678.64 | 1723.9608 | 45.3208 | 45.3208 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9179.62 | 1679.28 | 1723.9297 | 44.6497 | 44.6497 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9199.62 | 1679.78 | 1723.8985 | 44.1185 | 44.1185 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9219.63 | 1680.18 | 1723.8673 | 43.6873 | 43.6873 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9239.64 | 1680.99 | 1723.8362 | 42.8462 | 42.8462 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9259.67 | 1682.1 | 1723.805 | 41.705 | 41.705 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9275.48 | 1682.86 | 1723.7803 | 40.9203 | 40.9203 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9295.52 | 1681.67 | 1723.7491 | 42.0791 | 42.0791 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9315.52 | 1681.69 | 1723.718 | 42.028 | 42.028 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9335.52 | 1681.54 | 1723.6868 | 42.1468 | 42.1468 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9355.58 | 1683.06 | 1723.6556 | 40.5956 | 40.5956 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9375.59 | 1682.36 | 1723.6244 | 41.2644 | 41.2644 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9395.6 | 1683.16 | 1723.5932 | 40.4332 | 40.4332 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9415.64 | 1681.99 | 1723.562 | 41.572 | 41.572 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9435.64 | 1682.12 | 1723.5309 | 41.4109 | 41.4109 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9455.64 | 1682.29 | 1723.4997 | 41.2097 | 41.2097 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9475.86 | 1682.19 | 1723.4682 | 41.2782 | 41.2782 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9495.86 | 1682.46 | 1723.4371 | 40.9771 | 40.9771 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9515.87 | 1681.99 | 1723.4059 | 41.4159 | 41.4159 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9535.93 | 1683.59 | 1723.3747 | 39.7847 | 39.7847 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9555.96 | 1682.61 | 1723.3435 | 40.7335 | 40.7335 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9575.96 | 1682.82 | 1723.3123 | 40.4923 | 40.4923 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9595.97 | 1681.97 | 1723.2811 | 41.3111 | 41.3111 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9616.03 | 1683.45 | 1723.2499 | 39.7999 | 39.7999 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9636.04 | 1682.91 | 1723.2187 | 40.3087 | 40.3087 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9656.05 | 1682.33 | 1723.1875 | 40.8575 | 40.8575 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9676.06 | 1682.98 | 1723.1564 | 40.1764 | 40.1764 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9696.06 | 1683.16 | 1723.1252 | 39.9652 | 39.9652 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9716.06 | 1683.61 | 1723.0941 | 39.4841 | 39.4841 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9736.07 | 1684.16 | 1723.0629 | 38.9029 | 38.9029 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9756.07 | 1684.27 | 1723.0317 | 38.7617 | 38.7617 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9776.07 | 1684.52 | 1723.0006 | 38.4806 | 38.4806 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9796.08 | 1684.93 | 1722.9694 | 38.0394 | 38.0394 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9816.08 | 1684.97 | 1722.9383 | 37.9683 | 37.9683 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9836.08 | 1684.87 | 1722.9071 | 38.0371 | 38.0371 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9856.14 | 1686.51 | 1722.8759 | 36.3659 | 36.3659 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9876.14 | 1686.55 | 1722.8447 | 36.2947 | 36.2947 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9896.15 | 1687.03 | 1722.8135 | 35.7835 | 35.7835 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9916.16 | 1687.61 | 1722.7824 | 35.1724 | 35.1724 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9936.16 | 1687.85 | 1722.7512 | 34.9012 | 34.9012 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9956.16 | 1688.23 | 1722.7201 | 34.4901 | 34.4901 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9976.17 | 1688.73 | 1722.6889 | 33.9589 | 33.9589 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 9996.17 | 1689.06 | 1722.6578 | 33.5978 | 33.5978 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10016.18 | 1689.61 | 1722.6266 | 33.0166 | 33.0166 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10036.18 | 1689.74 | 1722.5954 | 32.8554 | 32.8554 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10056.19 | 1690.32 | 1722.5643 | 32.2443 | 32.2443 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10076.19 | 1690.58 | 1722.5331 | 31.9531 | 31.9531 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10096.19 | 1691.07 | 1722.502 | 31.432 | 31.432 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10116.21 | 1691.72 | 1722.4708 | 30.7508 | 30.7508 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10136.21 | 1691.96 | 1722.4396 | 30.4796 | 30.4796 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10156.21 | 1692.41 | 1722.4085 | 29.9985 | 29.9985 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10176.23 | 1693.16 | 1722.3773 | 29.2173 | 29.2173 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10196.23 | 1693.14 | 1722.3461 | 29.2061 | 29.2061 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10216.23 | 1693.26 | 1722.315 | 29.055 | 29.055 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10236.23 | 1693.57 | 1722.2838 | 28.7138 | 28.7138 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10256.23 | 1693.79 | 1722.2527 | 28.4627 | 28.4627 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10276.24 | 1694.28 | 1722.2215 | 27.9415 | 27.9415 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10296.24 | 1694.55 | 1722.1903 | 27.6403 | 27.6403 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10316.24 | 1694.79 | 1722.1592 | 27.3692 | 27.3692 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10336.24 | 1694.91 | 1722.128 | 27.218 | 27.218 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10356.24 | 1695.21 | 1722.0969 | 26.8869 | 26.8869 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10376.24 | 1694.94 | 1722.0657 | 27.1257 | 27.1257 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10396.24 | 1695.08 | 1722.0346 | 26.9546 | 26.9546 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10416.24 | 1695.04 | 1722.0034 | 26.9634 | 26.9634 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10436.25 | 1695.32 | 1721.9723 | 26.6523 | 26.6523 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10456.25 | 1695.19 | 1721.9411 | 26.7511 | 26.7511 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10476.25 | 1694.94 | 1721.9099 | 26.9699 | 26.9699 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10496.25 | 1694.92 | 1721.8788 | 26.9588 | 26.9588 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10516.25 | 1694.83 | 1721.8476 | 27.0176 | 27.0176 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10536.25 | 1694.4 | 1721.8165 | 27.4165 | 27.4165 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10556.25 | 1694.39 | 1721.7853 | 27.3953 | 27.3953 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10576.28 | 1693.31 | 1721.7541 | 28.4441 | 28.4441 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10596.28 | 1693.58 | 1721.723 | 28.143 | 28.143 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10616.29 | 1693.16 | 1721.6918 | 28.5318 | 28.5318 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10636.29 | 1693.01 | 1721.6607 | 28.6507 | 28.6507 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10656.3 | 1692.51 | 1721.6295 | 29.1195 | 29.1195 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10676.3 | 1692.11 | 1721.5983 | 29.4883 | 29.4883 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10696.3 | 1691.66 | 1721.5672 | 29.9072 | 29.9072 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10716.31 | 1691.39 | 1721.536 | 30.146 | 30.146 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10736.32 | 1690.71 | 1721.5048 | 30.7948 | 30.7948 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10756.32 | 1690.21 | 1721.4737 | 31.2637 | 31.2637 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10776.33 | 1689.89 | 1721.4425 | 31.5525 | 31.5525 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10796.35 | 1688.94 | 1721.4113 | 32.4713 | 32.4713 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10816.35 | 1688.71 | 1721.3802 | 32.6702 | 32.6702 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10836.36 | 1688.01 | 1721.349 | 33.339 | 33.339 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10856.36 | 1687.8 | 1721.3179 | 33.5179 | 33.5179 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10876.38 | 1687.07 | 1721.2867 | 34.2167 | 34.2167 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10896.38 | 1687 | 1721.2555 | 34.2555 | 34.2555 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10916.39 | 1686.34 | 1721.2244 | 34.8844 | 34.8844 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10936.4 | 1685.76 | 1721.1932 | 35.4332 | 35.4332 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10956.4 | 1685.72 | 1721.162 | 35.442 | 35.442 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10976.41 | 1685.11 | 1721.1309 | 36.0209 | 36.0209 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 10996.41 | 1684.9 | 1721.0997 | 36.1997 | 36.1997 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11015.91 | 1684.79 | 1721.0693 | 36.2793 | 36.2793 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11035.91 | 1684.3 | 1721.0382 | 36.7382 | 36.7382 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11055.91 | 1684.23 | 1721.007 | 36.777 | 36.777 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11075.91 | 1684.49 | 1720.9759 | 36.4859 | 36.4859 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11095.92 | 1684.15 | 1720.9447 | 36.7947 | 36.7947 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11115.92 | 1683.78 | 1720.9136 | 37.1336 | 37.1336 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11135.92 | 1683.68 | 1720.8824 | 37.2024 | 37.2024 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11155.92 | 1683.86 | 1720.8512 | 36.9912 | 36.9912 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11175.93 | 1683.43 | 1720.8201 | 37.3901 | 37.3901 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11195.93 | 1683.57 | 1720.7889 | 37.2189 | 37.2189 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11215.93 | 1683.56 | 1720.7578 | 37.1978 | 37.1978 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11235.85 | 1683.84 | 1720.7267 | 36.8867 | 36.8867 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11255.85 | 1683.68 | 1720.6956 | 37.0156 | 37.0156 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11275.85 | 1684.1 | 1720.6644 | 36.5644 | 36.5644 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11295.86 | 1683.82 | 1720.6333 | 36.8133 | 36.8133 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11315.86 | 1684.4 | 1720.6021 | 36.2021 | 36.2021 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11335.86 | 1684.42 | 1720.571 | 36.151 | 36.151 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11355.87 | 1684.69 | 1720.5398 | 35.8498 | 35.8498 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11375.87 | 1684.83 | 1720.5086 | 35.6786 | 35.6786 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11395.87 | 1684.94 | 1720.4775 | 35.5375 | 35.5375 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11415.87 | 1685.16 | 1720.4463 | 35.2863 | 35.2863 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11435.87 | 1685.23 | 1720.4152 | 35.1852 | 35.1852 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11455.89 | 1686.06 | 1720.384 | 34.324 | 34.324 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11475.89 | 1685.98 | 1720.3528 | 34.3728 | 34.3728 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11495.89 | 1685.87 | 1720.3217 | 34.4517 | 34.4517 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11515.89 | 1686.05 | 1720.2905 | 34.2405 | 34.2405 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11535.89 | 1686.12 | 1720.2594 | 34.1394 | 34.1394 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11555.89 | 1686.4 | 1720.2282 | 33.8282 | 33.8282 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11575.89 | 1686.79 | 1720.1971 | 33.4071 | 33.4071 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11595.89 | 1686.86 | 1720.1659 | 33.3059 | 33.3059 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11615.89 | 1687.09 | 1720.1348 | 33.0448 | 33.0448 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11635.9 | 1687.38 | 1720.1036 | 32.7236 | 32.7236 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11655.91 | 1688.06 | 1720.0724 | 32.0124 | 32.0124 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11675.91 | 1688.18 | 1720.0413 | 31.8613 | 31.8613 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11695.91 | 1687.98 | 1720.0101 | 32.0301 | 32.0301 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11715.91 | 1687.89 | 1719.979 | 32.089 | 32.089 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11735.92 | 1688.37 | 1719.9478 | 31.5778 | 31.5778 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11755.92 | 1688.53 | 1719.9166 | 31.3866 | 31.3866 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11775.92 | 1688.34 | 1719.8855 | 31.5455 | 31.5455 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11795.92 | 1688.43 | 1719.8543 | 31.4243 | 31.4243 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11815.92 | 1688.45 | 1719.8232 | 31.3732 | 31.3732 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11835.92 | 1688.48 | 1719.792 | 31.312 | 31.312 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11855.92 | 1688.24 | 1719.7609 | 31.5209 | 31.5209 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11875.92 | 1687.94 | 1719.7297 | 31.7897 | 31.7897 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11895.92 | 1687.88 | 1719.6986 | 31.8186 | 31.8186 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11915.93 | 1687.24 | 1719.6674 | 32.4274 | 32.4274 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11935.93 | 1687.24 | 1719.6363 | 32.3963 | 32.3963 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11955.93 | 1687.03 | 1719.6051 | 32.5751 | 32.5751 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11975.94 | 1686.46 | 1719.5739 | 33.1139 | 33.1139 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 11995.85 | 1686.95 | 1719.5429 | 32.5929 | 32.5929 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12015.86 | 1686.23 | 1719.5117 | 33.2817 | 33.2817 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12035.86 | 1686.23 | 1719.4806 | 33.2506 | 33.2506 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12055.86 | 1685.78 | 1719.4494 | 33.6694 | 33.6694 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12075.86 | 1685.78 | 1719.4183 | 33.6383 | 33.6383 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12095.88 | 1685.05 | 1719.3871 | 34.3371 | 34.3371 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12115.88 | 1684.83 | 1719.356 | 34.526 | 34.526 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12135.91 | 1683.68 | 1719.3248 | 35.6448 | 35.6448 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12155.92 | 1683.27 | 1719.2936 | 36.0236 | 36.0236 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12175.92 | 1683.62 | 1719.2624 | 35.6424 | 35.6424 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12195.99 | 1681.94 | 1719.2312 | 37.2912 | 37.2912 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12216.02 | 1680.85 | 1719.2 | 38.35 | 38.35 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12236.02 | 1680.5 | 1719.1688 | 38.6688 | 38.6688 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12256.05 | 1679.4 | 1719.1376 | 39.7376 | 39.7376 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12276.07 | 1678.46 | 1719.1064 | 40.6464 | 40.6464 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12296.13 | 1676.94 | 1719.0752 | 42.1352 | 42.1352 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12316.14 | 1676.37 | 1719.044 | 42.674 | 42.674 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12336.28 | 1673.98 | 1719.0126 | 45.0326 | 45.0326 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12356.28 | 1673.98 | 1718.9815 | 45.0015 | 45.0015 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12376.68 | 1669.97 | 1718.9497 | 48.9797 | 48.9797 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12396.68 | 1669.76 | 1718.9186 | 49.1586 | 49.1586 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12417 | 1666.2 | 1718.8869 | 52.6869 | 52.6869 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12437 | 1666.26 | 1718.8558 | 52.5958 | 52.5958 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12457 | 1666.26 | 1718.8246 | 52.5646 | 52.5646 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12477.68 | 1661 | 1718.7924 | 57.7924 | 57.7924 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12497.68 | 1661.01 | 1718.7612 | 57.7512 | 57.7512 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12517.69 | 1660.67 | 1718.7301 | 58.0601 | 58.0601 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12537.71 | 1659.86 | 1718.6989 | 58.8389 | 58.8389 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12557.71 | 1659.86 | 1718.6677 | 58.8077 | 58.8077 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12577.71 | 1659.36 | 1718.6366 | 59.2766 | 59.2766 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12597.74 | 1658.3 | 1718.6054 | 60.3054 | 60.3054 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12617.74 | 1658.3 | 1718.5742 | 60.2742 | 60.2742 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12637.74 | 1658.07 | 1718.5431 | 60.4731 | 60.4731 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12657.83 | 1656.24 | 1718.5118 | 62.2718 | 62.2718 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12677.84 | 1657.09 | 1718.4806 | 61.3906 | 61.3906 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12697.89 | 1655.71 | 1718.4494 | 62.7394 | 62.7394 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12718.02 | 1653.46 | 1718.418 | 64.958 | 64.958 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12738.05 | 1652.27 | 1718.3868 | 66.1168 | 66.1168 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12758.28 | 1650.48 | 1718.3553 | 67.8753 | 67.8753 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12778.34 | 1648.95 | 1718.3241 | 69.3741 | 69.3741 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12798.38 | 1650.25 | 1718.2928 | 68.0428 | 68.0428 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12818.45 | 1651.94 | 1718.2616 | 66.3216 | 66.3216 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12838.61 | 1654.42 | 1718.2302 | 63.8102 | 63.8102 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12858.61 | 1654.47 | 1718.199 | 63.729 | 63.729 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12878.84 | 1657.54 | 1718.1675 | 60.6275 | 60.6275 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12898.85 | 1658.16 | 1718.1363 | 59.9763 | 59.9763 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12918.91 | 1659.76 | 1718.1051 | 58.3451 | 58.3451 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12939.1 | 1662.5 | 1718.0737 | 55.5737 | 55.5737 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12959.14 | 1661.34 | 1718.0424 | 56.7024 | 56.7024 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12979.15 | 1660.64 | 1718.0113 | 57.3713 | 57.3713 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 12999.15 | 1660.36 | 1717.9801 | 57.6201 | 57.6201 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13019.15 | 1660.83 | 1717.949 | 57.119 | 57.119 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13039.17 | 1660.18 | 1717.9178 | 57.7378 | 57.7378 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13059.19 | 1659.18 | 1717.8866 | 58.7066 | 58.7066 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13079.3 | 1661.24 | 1717.8553 | 56.6153 | 56.6153 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13099.44 | 1658.86 | 1717.8239 | 58.9639 | 58.9639 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13118.99 | 1660.03 | 1717.7934 | 57.7634 | 57.7634 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13139.07 | 1658.31 | 1717.7622 | 59.4522 | 59.4522 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13159.17 | 1656.24 | 1717.7309 | 61.4909 | 61.4909 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13179.18 | 1655.81 | 1717.6997 | 61.8897 | 61.8897 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13199.64 | 1651.47 | 1717.6678 | 66.1978 | 66.1978 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13219.88 | 1654.53 | 1717.6363 | 63.1063 | 63.1063 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13240.66 | 1659.45 | 1717.6039 | 58.1539 | 58.1539 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13260.87 | 1662.35 | 1717.5724 | 55.2224 | 55.2224 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13280.97 | 1664.35 | 1717.5411 | 53.1911 | 53.1911 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13301.21 | 1667.51 | 1717.5096 | 49.9996 | 49.9996 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13321.22 | 1667.98 | 1717.4784 | 49.4984 | 49.4984 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13341.63 | 1672.08 | 1717.4466 | 45.3666 | 45.3666 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13361.79 | 1674.54 | 1717.4152 | 42.8752 | 42.8752 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13381.97 | 1677.27 | 1717.3838 | 40.1138 | 40.1138 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13401.97 | 1677.27 | 1717.3527 | 40.0827 | 40.0827 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13422.48 | 1681.83 | 1717.3207 | 35.4907 | 35.4907 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13442.62 | 1684.15 | 1717.2893 | 33.1393 | 33.1393 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13462.79 | 1684.74 | 1717.2579 | 32.5179 | 32.5179 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13482.88 | 1686.66 | 1717.2266 | 30.5666 | 30.5666 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13502.97 | 1688.61 | 1717.1953 | 28.5853 | 28.5853 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13523.11 | 1690.94 | 1717.164 | 26.224 | 26.224 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13543.12 | 1691.59 | 1717.1328 | 25.5428 | 25.5428 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13562.72 | 1691.57 | 1717.1023 | 25.5323 | 25.5323 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13582.73 | 1692.03 | 1717.0711 | 25.0411 | 25.0411 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13602.74 | 1692.86 | 1717.0399 | 24.1799 | 24.1799 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13622.74 | 1693.18 | 1717.0088 | 23.8288 | 23.8288 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13642.74 | 1693.21 | 1716.9776 | 23.7676 | 23.7676 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13662.74 | 1693.17 | 1716.9465 | 23.7765 | 23.7765 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13682.75 | 1693.64 | 1716.9153 | 23.2753 | 23.2753 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13702.58 | 1693.73 | 1716.8844 | 23.1544 | 23.1544 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13722.58 | 1693.73 | 1716.8533 | 23.1233 | 23.1233 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13742.58 | 1693.41 | 1716.8221 | 23.4121 | 23.4121 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13762.59 | 1693.77 | 1716.7909 | 23.0209 | 23.0209 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13782.59 | 1693.44 | 1716.7598 | 23.3198 | 23.3198 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13802.6 | 1694.08 | 1716.7286 | 22.6486 | 22.6486 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13822.6 | 1694.07 | 1716.6975 | 22.6275 | 22.6275 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13842.6 | 1694.17 | 1716.6663 | 22.4963 | 22.4963 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13862.6 | 1694.3 | 1716.6351 | 22.3351 | 22.3351 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13882.6 | 1694.15 | 1716.604 | 22.454 | 22.454 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13902.6 | 1694.55 | 1716.5728 | 22.0228 | 22.0228 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13922.6 | 1694.59 | 1716.5417 | 21.9517 | 21.9517 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13942.6 | 1694.69 | 1716.5105 | 21.8205 | 21.8205 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13962.61 | 1695.03 | 1716.4794 | 21.4494 | 21.4494 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 13982.54 | 1695.72 | 1716.4483 | 20.7283 | 20.7283 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14002.54 | 1696.07 | 1716.4172 | 20.3472 | 20.3472 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14022.54 | 1696.07 | 1716.386 | 20.316 | 20.316 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14042.54 | 1696.34 | 1716.3549 | 20.0149 | 20.0149 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14062.55 | 1696.52 | 1716.3237 | 19.8037 | 19.8037 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14082.57 | 1697.54 | 1716.2925 | 18.7525 | 18.7525 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14102.57 | 1697.48 | 1716.2614 | 18.7814 | 18.7814 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14122.57 | 1697.73 | 1716.2302 | 18.5002 | 18.5002 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14142.45 | 1698.38 | 1716.1992 | 17.8192 | 17.8192 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14162.46 | 1698.65 | 1716.1681 | 17.5181 | 17.5181 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14182.46 | 1699.23 | 1716.1369 | 16.9069 | 16.9069 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14202.48 | 1700.11 | 1716.1057 | 15.9957 | 15.9957 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14222.65 | 1700.33 | 1716.0743 | 15.7443 | 15.7443 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14242.66 | 1700.52 | 1716.0431 | 15.5231 | 15.5231 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14262.66 | 1700.83 | 1716.012 | 15.182 | 15.182 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14282.66 | 1700.98 | 1715.9808 | 15.0008 | 15.0008 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14302.66 | 1700.98 | 1715.9497 | 14.9697 | 14.9697 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14322.7 | 1702.3 | 1715.9185 | 13.6185 | 13.6185 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14342.63 | 1702.9 | 1715.8874 | 12.9874 | 12.9874 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14362.63 | 1703.02 | 1715.8563 | 12.8363 | 12.8363 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14382.63 | 1703.35 | 1715.8251 | 12.4751 | 12.4751 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14402.66 | 1704.43 | 1715.7939 | 11.3639 | 11.3639 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14422.72 | 1705.48 | 1715.7627 | 10.2827 | 10.2827 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14442.74 | 1706.38 | 1715.7315 | 9.3515 | 9.3515 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14462.76 | 1707.25 | 1715.7003 | 8.4503 | 8.4503 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14482.76 | 1707.44 | 1715.6691 | 8.2291 | 8.2291 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14502.77 | 1707.98 | 1715.638 | 7.658 | 7.658 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14522.92 | 1708.35 | 1715.6066 | 7.2566 | 7.2566 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14542.92 | 1708.57 | 1715.5754 | 7.0054 | 7.0054 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14563.14 | 1708.76 | 1715.5439 | 6.7839 | 6.7839 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14583.14 | 1708.84 | 1715.5128 | 6.6728 | 6.6728 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14603.14 | 1708.66 | 1715.4816 | 6.8216 | 6.8216 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14623.38 | 1707.86 | 1715.4501 | 7.5901 | 7.5901 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14643.4 | 1706.87 | 1715.4189 | 8.5489 | 8.5489 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14663.4 | 1706.82 | 1715.3878 | 8.5678 | 8.5678 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14683.45 | 1705.52 | 1715.3565 | 9.8365 | 9.8365 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14703.45 | 1705.61 | 1715.3254 | 9.7154 | 9.7154 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14723.49 | 1704.38 | 1715.2942 | 10.9142 | 10.9142 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14743.49 | 1704.38 | 1715.263 | 10.883 | 10.883 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14763.43 | 1703.86 | 1715.232 | 11.372 | 11.372 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14783.45 | 1702.92 | 1715.2008 | 12.2808 | 12.2808 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14803.46 | 1702.63 | 1715.1696 | 12.5396 | 12.5396 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14823.49 | 1701.44 | 1715.1384 | 13.6984 | 13.6984 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14843.49 | 1701.19 | 1715.1072 | 13.9172 | 13.9172 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14863.51 | 1700.33 | 1715.0761 | 14.7461 | 14.7461 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14883.52 | 1699.71 | 1715.0449 | 15.3349 | 15.3349 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14903.53 | 1699.19 | 1715.0137 | 15.8237 | 15.8237 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14923.54 | 1698.62 | 1714.9826 | 16.3626 | 16.3626 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14943.55 | 1697.92 | 1714.9514 | 17.0314 | 17.0314 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14963.56 | 1697.28 | 1714.9202 | 17.6402 | 17.6402 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 14983.57 | 1696.71 | 1714.8891 | 18.1791 | 18.1791 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15003.57 | 1696.54 | 1714.8579 | 18.3179 | 18.3179 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15023.58 | 1695.74 | 1714.8267 | 19.0867 | 19.0867 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15043.59 | 1695.24 | 1714.7956 | 19.5556 | 19.5556 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15063.59 | 1694.82 | 1714.7644 | 19.9444 | 19.9444 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15083.6 | 1694.52 | 1714.7332 | 20.2132 | 20.2132 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15103.6 | 1694.86 | 1714.7021 | 19.8421 | 19.8421 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15123.6 | 1694.86 | 1714.6709 | 19.8109 | 19.8109 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15143.67 | 1693.13 | 1714.6397 | 21.5097 | 21.5097 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15163.68 | 1692.76 | 1714.6085 | 21.8485 | 21.8485 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15183.68 | 1692.23 | 1714.5773 | 22.3473 | 22.3473 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15203.76 | 1691.89 | 1714.5461 | 22.6561 | 22.6561 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15223.76 | 1691.89 | 1714.5149 | 22.6249 | 22.6249 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15243.76 | 1691.56 | 1714.4838 | 22.9238 | 22.9238 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15263.76 | 1691.42 | 1714.4526 | 23.0326 | 23.0326 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15283.76 | 1691.12 | 1714.4215 | 23.3015 | 23.3015 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15303.76 | 1691.32 | 1714.3903 | 23.0703 | 23.0703 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15323.78 | 1690.43 | 1714.3591 | 23.9291 | 23.9291 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15343.81 | 1691.47 | 1714.3279 | 22.8579 | 22.8579 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15363.83 | 1690.64 | 1714.2967 | 23.6567 | 23.6567 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15383.83 | 1690.21 | 1714.2656 | 24.0556 | 24.0556 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15403.79 | 1690.19 | 1714.2345 | 24.0445 | 24.0445 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15423.79 | 1689.99 | 1714.2033 | 24.2133 | 24.2133 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15443.8 | 1689.47 | 1714.1722 | 24.7022 | 24.7022 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15463.8 | 1689.55 | 1714.141 | 24.591 | 24.591 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15483.8 | 1689.52 | 1714.1099 | 24.5899 | 24.5899 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15503.8 | 1689.3 | 1714.0787 | 24.7787 | 24.7787 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15523.8 | 1689.3 | 1714.0476 | 24.7476 | 24.7476 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15543.8 | 1689.15 | 1714.0164 | 24.8664 | 24.8664 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15563.8 | 1689.25 | 1713.9852 | 24.7352 | 24.7352 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15583.8 | 1689.2 | 1713.9541 | 24.7541 | 24.7541 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15603.8 | 1689.06 | 1713.9229 | 24.8629 | 24.8629 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15623.82 | 1688.25 | 1713.8918 | 25.6418 | 25.6418 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15643.82 | 1688.25 | 1713.8606 | 25.6106 | 25.6106 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15663.82 | 1687.78 | 1713.8294 | 26.0494 | 26.0494 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15683.82 | 1687.78 | 1713.7983 | 26.0183 | 26.0183 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15703.82 | 1687.74 | 1713.7671 | 26.0271 | 26.0271 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15723.83 | 1687.48 | 1713.736 | 26.256 | 26.256 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15743.84 | 1686.82 | 1713.7048 | 26.8848 | 26.8848 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15763.84 | 1686.42 | 1713.6737 | 27.2537 | 27.2537 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15783.84 | 1686.5 | 1713.6425 | 27.1425 | 27.1425 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15803.84 | 1686.24 | 1713.6113 | 27.3713 | 27.3713 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15823.84 | 1686.24 | 1713.5802 | 27.3402 | 27.3402 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15843.85 | 1685.59 | 1713.549 | 27.959 | 27.959 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15863.85 | 1685.59 | 1713.5179 | 27.9279 | 27.9279 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15883.86 | 1685.04 | 1713.4867 | 28.4467 | 28.4467 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15903.86 | 1685.04 | 1713.4555 | 28.4155 | 28.4155 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15923.87 | 1684.37 | 1713.4244 | 29.0544 | 29.0544 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15943.87 | 1684.37 | 1713.3932 | 29.0232 | 29.0232 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15963.87 | 1684.2 | 1713.3621 | 29.1621 | 29.1621 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 15983.87 | 1684.2 | 1713.3309 | 29.1309 | 29.1309 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16003.88 | 1683.55 | 1713.2997 | 29.7497 | 29.7497 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16023.88 | 1683.55 | 1713.2686 | 29.7186 | 29.7186 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16043.88 | 1683.38 | 1713.2374 | 29.8574 | 29.8574 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16063.89 | 1683.16 | 1713.2063 | 30.0463 | 30.0463 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16083.89 | 1682.8 | 1713.1751 | 30.3751 | 30.3751 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16103.89 | 1682.76 | 1713.144 | 30.384 | 30.384 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16123.89 | 1682.43 | 1713.1128 | 30.6828 | 30.6828 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16143.89 | 1682.34 | 1713.0817 | 30.7417 | 30.7417 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16163.9 | 1682.77 | 1713.0505 | 30.2805 | 30.2805 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16183.9 | 1682.33 | 1713.0193 | 30.6893 | 30.6893 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16203.9 | 1682.14 | 1712.9882 | 30.8482 | 30.8482 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16223.9 | 1681.96 | 1712.957 | 30.997 | 30.997 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16243.91 | 1681.38 | 1712.9259 | 31.5459 | 31.5459 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16263.91 | 1681.38 | 1712.8947 | 31.5147 | 31.5147 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16283.91 | 1681.27 | 1712.8636 | 31.5936 | 31.5936 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16303.89 | 1681.2 | 1712.8324 | 31.6324 | 31.6324 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16323.89 | 1680.97 | 1712.8013 | 31.8313 | 31.8313 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16343.89 | 1680.89 | 1712.7701 | 31.8801 | 31.8801 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16363.89 | 1680.91 | 1712.739 | 31.829 | 31.829 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16383.9 | 1680.45 | 1712.7078 | 32.2578 | 32.2578 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16403.9 | 1680.45 | 1712.6767 | 32.2267 | 32.2267 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16423.9 | 1680.59 | 1712.6455 | 32.0555 | 32.0555 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16443.9 | 1680.49 | 1712.6143 | 32.1243 | 32.1243 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16463.9 | 1680.49 | 1712.5832 | 32.0932 | 32.0932 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16483.91 | 1681.06 | 1712.552 | 31.492 | 31.492 | 10 | 16
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16503.91 | 1681.31 | 1712.5209 | 31.2109 | 31.2109 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16523.91 | 1681.51 | 1712.4897 | 30.9797 | 30.9797 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16543.91 | 1681.79 | 1712.4586 | 30.6686 | 30.6686 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16563.91 | 1681.79 | 1712.4274 | 30.6374 | 30.6374 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16584.01 | 1683.81 | 1712.3961 | 28.5861 | 28.5861 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16604.02 | 1684.21 | 1712.3649 | 28.1549 | 28.1549 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16624.07 | 1685.59 | 1712.3337 | 26.7437 | 26.7437 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16644.07 | 1685.11 | 1712.3025 | 27.1925 | 27.1925 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16664.1 | 1686.19 | 1712.2713 | 26.0813 | 26.0813 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16684.1 | 1686.56 | 1712.2402 | 25.6802 | 25.6802 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16704.11 | 1687.16 | 1712.209 | 25.049 | 25.049 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16724.12 | 1687.82 | 1712.1779 | 24.3579 | 24.3579 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16744.12 | 1687.87 | 1712.1467 | 24.2767 | 24.2767 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16764.13 | 1688.35 | 1712.1155 | 23.7655 | 23.7655 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16784.13 | 1688.35 | 1712.0844 | 23.7344 | 23.7344 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16804.22 | 1690.23 | 1712.0531 | 21.8231 | 21.8231 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16824.22 | 1690.67 | 1712.0219 | 21.3519 | 21.3519 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16844.25 | 1692.07 | 1711.9907 | 19.9207 | 19.9207 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16864.27 | 1692.87 | 1711.9596 | 19.0896 | 19.0896 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16884.27 | 1693.28 | 1711.9284 | 18.6484 | 18.6484 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16904.3 | 1694.28 | 1711.8972 | 17.6172 | 17.6172 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16924.41 | 1694.7 | 1711.8659 | 17.1659 | 17.1659 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16944.41 | 1694.8 | 1711.8347 | 17.0347 | 17.0347 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16964.43 | 1695.73 | 1711.8035 | 16.0735 | 16.0735 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 16984.57 | 1695.38 | 1711.7722 | 16.3922 | 16.3922 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17004.59 | 1696.33 | 1711.741 | 15.411 | 15.411 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17024.59 | 1696.81 | 1711.7098 | 14.8998 | 14.8998 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17044.6 | 1696.52 | 1711.6787 | 15.1587 | 15.1587 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17064.6 | 1697.05 | 1711.6475 | 14.5975 | 14.5975 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17084.6 | 1697.03 | 1711.6164 | 14.5864 | 14.5864 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17104.6 | 1696.9 | 1711.5852 | 14.6852 | 14.6852 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17124.6 | 1696.98 | 1711.554 | 14.574 | 14.574 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17144.6 | 1696.98 | 1711.5229 | 14.5429 | 14.5429 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17164.61 | 1696.35 | 1711.4917 | 15.1417 | 15.1417 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17184.63 | 1697.07 | 1711.4605 | 14.3905 | 14.3905 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17204.68 | 1695.57 | 1711.4293 | 15.8593 | 15.8593 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17224.68 | 1695.51 | 1711.3982 | 15.8882 | 15.8882 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17244.71 | 1694.42 | 1711.367 | 16.947 | 16.947 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17264.71 | 1694.42 | 1711.3358 | 16.9158 | 16.9158 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17284.71 | 1694.17 | 1711.3046 | 17.1346 | 17.1346 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17304.73 | 1693.42 | 1711.2735 | 17.8535 | 17.8535 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17324.73 | 1693.69 | 1711.2423 | 17.5523 | 17.5523 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17344.73 | 1693.54 | 1711.2112 | 17.6712 | 17.6712 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17364.82 | 1693.89 | 1711.1799 | 17.2899 | 17.2899 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17384.82 | 1693.89 | 1711.1487 | 17.2587 | 17.2587 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17404.82 | 1693.79 | 1711.1176 | 17.3276 | 17.3276 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17424.83 | 1694 | 1711.0864 | 17.0864 | 17.0864 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17444.83 | 1694.48 | 1711.0552 | 16.5752 | 16.5752 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17464.83 | 1694.4 | 1711.0241 | 16.6241 | 16.6241 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17484.83 | 1694.31 | 1710.9929 | 16.6829 | 16.6829 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17504.83 | 1694.69 | 1710.9618 | 16.2718 | 16.2718 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17524.84 | 1694.5 | 1710.9306 | 16.4306 | 16.4306 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17544.84 | 1694.39 | 1710.8995 | 16.5095 | 16.5095 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17564.84 | 1694.57 | 1710.8683 | 16.2983 | 16.2983 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17584.84 | 1694.47 | 1710.8371 | 16.3671 | 16.3671 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17604.84 | 1694.77 | 1710.806 | 16.036 | 16.036 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17624.84 | 1695.1 | 1710.7748 | 15.6748 | 15.6748 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17644.84 | 1694.81 | 1710.7437 | 15.9337 | 15.9337 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17664.85 | 1695.1 | 1710.7125 | 15.6125 | 15.6125 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17684.85 | 1694.86 | 1710.6814 | 15.8214 | 15.8214 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17704.85 | 1694.72 | 1710.6502 | 15.9302 | 15.9302 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17724.85 | 1694.75 | 1710.6191 | 15.8691 | 15.8691 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17744.85 | 1694.75 | 1710.5879 | 15.8379 | 15.8379 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17764.86 | 1694.6 | 1710.5567 | 15.9567 | 15.9567 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17784.87 | 1695.17 | 1710.5256 | 15.3556 | 15.3556 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17804.88 | 1694.36 | 1710.4944 | 16.1344 | 16.1344 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17824.88 | 1694.33 | 1710.4632 | 16.1332 | 16.1332 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17844.88 | 1694.33 | 1710.4321 | 16.1021 | 16.1021 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17864.89 | 1695 | 1710.4009 | 15.4009 | 15.4009 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17884.89 | 1694.95 | 1710.3698 | 15.4198 | 15.4198 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17904.94 | 1693.65 | 1710.3385 | 16.6885 | 16.6885 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17925.13 | 1694.13 | 1710.3071 | 16.1771 | 16.1771 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17945.14 | 1694.75 | 1710.2759 | 15.5259 | 15.5259 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17965.15 | 1695.38 | 1710.2447 | 14.8647 | 14.8647 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 17985.15 | 1695.44 | 1710.2136 | 14.7736 | 14.7736 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18005.16 | 1694.82 | 1710.1824 | 15.3624 | 15.3624 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18025.16 | 1694.82 | 1710.1513 | 15.3313 | 15.3313 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18045.57 | 1694.89 | 1710.1195 | 15.2295 | 15.2295 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18065.58 | 1695.52 | 1710.0883 | 14.5683 | 14.5683 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18085.59 | 1694.81 | 1710.0571 | 15.2471 | 15.2471 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18105.61 | 1695.62 | 1710.026 | 14.406 | 14.406 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18125.61 | 1695.88 | 1709.9948 | 14.1148 | 14.1148 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18145.61 | 1695.82 | 1709.9637 | 14.1437 | 14.1437 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18165.61 | 1695.97 | 1709.9325 | 13.9625 | 13.9625 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18185.62 | 1696.26 | 1709.9013 | 13.6413 | 13.6413 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18205.62 | 1696.01 | 1709.8702 | 13.8602 | 13.8602 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18225.62 | 1696.55 | 1709.839 | 13.289 | 13.289 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18245.63 | 1696.18 | 1709.8079 | 13.6279 | 13.6279 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18265.63 | 1696.49 | 1709.7767 | 13.2867 | 13.2867 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18285.63 | 1696.59 | 1709.7455 | 13.1555 | 13.1555 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18305.63 | 1696.61 | 1709.7144 | 13.1044 | 13.1044 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18325.63 | 1696.6 | 1709.6832 | 13.0832 | 13.0832 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18345.63 | 1696.42 | 1709.6521 | 13.2321 | 13.2321 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18365.63 | 1696.42 | 1709.6209 | 13.2009 | 13.2009 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18385.63 | 1696.03 | 1709.5898 | 13.5598 | 13.5598 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18405.64 | 1695.7 | 1709.5586 | 13.8586 | 13.8586 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18425.64 | 1695.7 | 1709.5275 | 13.8275 | 13.8275 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18445.64 | 1695.69 | 1709.4963 | 13.8063 | 13.8063 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18465.64 | 1696.03 | 1709.4652 | 13.4352 | 13.4352 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18485.64 | 1695.99 | 1709.434 | 13.444 | 13.444 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18505.64 | 1695.85 | 1709.4028 | 13.5528 | 13.5528 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18525.65 | 1695.26 | 1709.3717 | 14.1117 | 14.1117 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18545.65 | 1695.08 | 1709.3405 | 14.2605 | 14.2605 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18565.65 | 1694.85 | 1709.3094 | 14.4594 | 14.4594 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18585.66 | 1694.48 | 1709.2782 | 14.7982 | 14.7982 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18605.69 | 1695.65 | 1709.247 | 13.597 | 13.597 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18625.7 | 1695.15 | 1709.2158 | 14.0658 | 14.0658 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18645.74 | 1693.75 | 1709.1846 | 15.4346 | 15.4346 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18665.74 | 1693.84 | 1709.1535 | 15.3135 | 15.3135 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18685.75 | 1694.02 | 1709.1223 | 15.1023 | 15.1023 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18705.76 | 1693.26 | 1709.0911 | 15.8311 | 15.8311 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18725.78 | 1692.34 | 1709.0599 | 16.7199 | 16.7199 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18745.78 | 1692.34 | 1709.0288 | 16.6888 | 16.6888 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18765.78 | 1692.43 | 1708.9976 | 16.5676 | 16.5676 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18785.78 | 1692.43 | 1708.9665 | 16.5365 | 16.5365 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18805.78 | 1692.17 | 1708.9353 | 16.7653 | 16.7653 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18825.81 | 1691.16 | 1708.9041 | 17.7441 | 17.7441 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18845.84 | 1692.22 | 1708.8729 | 16.6529 | 16.6529 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18865.92 | 1690.44 | 1708.8417 | 18.4017 | 18.4017 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18885.92 | 1690.36 | 1708.8105 | 18.4505 | 18.4505 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18905.93 | 1689.72 | 1708.7793 | 19.0593 | 19.0593 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18925.93 | 1689.9 | 1708.7482 | 18.8482 | 18.8482 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18945.93 | 1689.79 | 1708.717 | 18.927 | 18.927 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18965.93 | 1689.89 | 1708.6859 | 18.7959 | 18.7959 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 18985.93 | 1689.43 | 1708.6547 | 19.2247 | 19.2247 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19005.93 | 1689.54 | 1708.6236 | 19.0836 | 19.0836 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19025.93 | 1689.45 | 1708.5924 | 19.1424 | 19.1424 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19045.93 | 1689.71 | 1708.5613 | 18.8513 | 18.8513 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19065.94 | 1689.19 | 1708.5301 | 19.3401 | 19.3401 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19085.95 | 1689.75 | 1708.4989 | 18.7489 | 18.7489 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19105.95 | 1689.75 | 1708.4678 | 18.7178 | 18.7178 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19126 | 1690.36 | 1708.4365 | 18.0765 | 18.0765 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19146 | 1690.62 | 1708.4054 | 17.7854 | 17.7854 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19166 | 1690.95 | 1708.3742 | 17.4242 | 17.4242 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19186 | 1691.13 | 1708.3431 | 17.2131 | 17.2131 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19206.01 | 1691.53 | 1708.3119 | 16.7819 | 16.7819 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19226.01 | 1691.59 | 1708.2808 | 16.6908 | 16.6908 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19246.05 | 1692.88 | 1708.2495 | 15.3695 | 15.3695 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19266.1 | 1692.99 | 1708.2183 | 15.2283 | 15.2283 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19286.11 | 1693.51 | 1708.1871 | 14.6771 | 14.6771 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19306.13 | 1694.48 | 1708.156 | 13.676 | 13.676 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19326.14 | 1694.94 | 1708.1248 | 13.1848 | 13.1848 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19346.15 | 1695.69 | 1708.0936 | 12.4036 | 12.4036 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19366.5 | 1695.86 | 1708.0619 | 12.2019 | 12.2019 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19386.51 | 1696.39 | 1708.0307 | 11.6407 | 11.6407 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19406.51 | 1696.57 | 1707.9996 | 11.4296 | 11.4296 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19426.54 | 1696.9 | 1707.9684 | 11.0684 | 11.0684 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19446.54 | 1697.09 | 1707.9372 | 10.8472 | 10.8472 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19466.82 | 1697.43 | 1707.9056 | 10.4756 | 10.4756 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19486.82 | 1697.47 | 1707.8745 | 10.4045 | 10.4045 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19506.82 | 1697.47 | 1707.8433 | 10.3733 | 10.3733 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19526.83 | 1697.7 | 1707.8122 | 10.1122 | 10.1122 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19546.7 | 1697.87 | 1707.7812 | 9.9112 | 9.9112 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19566.71 | 1697.16 | 1707.7501 | 10.5901 | 10.5901 | 10 | 10
BPS_RM_1 | NKANGAMO_BPS | J-001N | 19581.43 | 1697.14 | 1707.7271 | 10.5871 | 10.5871 | 10 | 10
BPS_RM_2 | J-001N | J-002N | 0 | 1697.14 | 1707.7271 | 10.5871 | 10.5871 | 10 | 10
BPS_RM_2 | J-001N | J-002N | 20.02 | 1697.98 | 1707.697 | 9.717 | 9.717 | 10 | 10
BPS_RM_2 | J-001N | J-002N | 40.02 | 1698.05 | 1707.6669 | 9.6169 | 9.6169 | 10 | 10
BPS_RM_3 | J-002N | J-003N | 0 | 1698.05 | 1707.6669 | 9.6169 | 9.6169 | 10 | 10
BPS_RM_3 | J-002N | J-003N | 20 | 1698.4 | 1707.6411 | 9.2411 | 9.2411 | 10 | 10
BPS_RM_3 | J-002N | J-003N | 40.27 | 1698.23 | 1707.6149 | 9.3849 | 9.3849 | 10 | 10
BPS_RM_3 | J-002N | J-003N | 60.27 | 1698.23 | 1707.589 | 9.359 | 9.359 | 10 | 10
BPS_RM_3 | J-002N | J-003N | 80.25 | 1698.29 | 1707.5632 | 9.2732 | 9.2732 | 10 | 10
BPS_RM_3 | J-002N | J-003N | 100.25 | 1698.14 | 1707.5374 | 9.3974 | 9.3974 | 10 | 10
UHURU_INLET | J-003N | UHURU_PARK_GBR | 0 | 1698.14 | 1707.5374 | 9.3974 | 9.3974 | 10 | 10
UHURU_INLET | J-003N | UHURU_PARK_GBR | 50 | 1696.1 | 1707.4768 | 11.3768 | 11.3768 | 10 | 10
ESR_BRANCH | J-001N | TUNDUMA_ESR | 0 | 1697.14 | 1707.7271 | 10.5871 | 10.5871 | 10 | 10
ESR_BRANCH | J-001N | TUNDUMA_ESR | 38 | 1698.8 | 1707.5 | 8.7 | 8.7 | 10 | 10
GSR01_BRANCH | J-002N | UHURU_GSR01 | 0 | 1698.05 | 1707.6669 | 9.6169 | 9.6169 | 10 | 10
GSR01_BRANCH | J-002N | UHURU_GSR01 | 40 | 1697.2 | 1707.2013 | 10.0013 | 10.0013 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 0 | 1698.14 | 1707.5374 | 9.3974 | 9.3974 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 104.99 | 1698.3 | 1707.3111 | 9.0111 | 9.0111 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 124.99 | 1698.19 | 1707.268 | 9.078 | 9.078 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 144.99 | 1698.25 | 1707.2249 | 8.9749 | 8.9749 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 164.99 | 1698.12 | 1707.1818 | 9.0618 | 9.0618 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 296.09 | 1692.73 | 1706.8993 | 14.1693 | 14.1693 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 377.83 | 1683.81 | 1706.7231 | 22.9131 | 22.9131 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 424.97 | 1678.89 | 1706.6215 | 27.7315 | 27.7315 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 475.02 | 1681.21 | 1706.5136 | 25.3036 | 25.3036 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 525.03 | 1680.53 | 1706.4059 | 25.8759 | 25.97 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 569.16 | 1677.84 | 1706.3108 | 28.4708 | 28.66 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 619.25 | 1674.76 | 1706.2028 | 31.4428 | 31.74 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 669.3 | 1672.61 | 1706.0949 | 33.4849 | 33.89 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 719.31 | 1671.53 | 1705.9872 | 34.4572 | 34.97 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 769.33 | 1670.3 | 1705.8794 | 35.5794 | 36.2 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 819.34 | 1669.15 | 1705.7716 | 36.6216 | 37.35 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 869.35 | 1668.15 | 1705.6638 | 37.5138 | 38.35 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 919.35 | 1668.03 | 1705.5561 | 37.5261 | 38.47 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 969.35 | 1668.31 | 1705.4483 | 37.1383 | 38.19 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1019.35 | 1668.75 | 1705.3405 | 36.5905 | 37.75 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1069.35 | 1668.45 | 1705.2328 | 36.7828 | 38.05 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1119.35 | 1668.6 | 1705.125 | 36.525 | 37.9 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1169.35 | 1668.29 | 1705.0173 | 36.7273 | 38.21 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1219.36 | 1667.64 | 1704.9095 | 37.2695 | 38.86 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1269.36 | 1667.29 | 1704.8018 | 37.5118 | 39.21 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1319.36 | 1667.25 | 1704.694 | 37.444 | 39.25 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1369.36 | 1667.6 | 1704.5862 | 36.9862 | 38.9 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1419.36 | 1668.11 | 1704.4785 | 36.3685 | 38.39 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1469.36 | 1667.91 | 1704.3707 | 36.4607 | 38.59 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1519.37 | 1668.67 | 1704.263 | 35.593 | 37.83 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1569.37 | 1668.1 | 1704.1552 | 36.0552 | 38.4 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1612.23 | 1668.83 | 1704.0628 | 35.2328 | 37.67 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1662.23 | 1669.33 | 1703.9551 | 34.6251 | 37.17 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1712.24 | 1668.57 | 1703.8473 | 35.2773 | 37.93 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1753.71 | 1666.22 | 1703.7579 | 37.5379 | 40.28 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1803.72 | 1665.6 | 1703.6501 | 38.0501 | 40.9 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1853.66 | 1664.54 | 1703.5425 | 39.0025 | 41.96 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1903.67 | 1663.7 | 1703.4347 | 39.7347 | 42.8 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 1953.73 | 1661.13 | 1703.3269 | 42.1969 | 45.37 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2003.88 | 1657.29 | 1703.2188 | 45.9288 | 49.21 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2054.14 | 1653.07 | 1703.1105 | 50.0405 | 53.43 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2102.01 | 1650.7 | 1703.0073 | 52.3073 | 55.8 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2146.65 | 1647.75 | 1702.9111 | 55.1611 | 58.75 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2196.74 | 1644.78 | 1702.8031 | 58.0231 | 61.72 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2245.55 | 1641.64 | 1702.698 | 61.058 | 64.86 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2284.56 | 1638.68 | 1702.6139 | 63.9339 | 67.82 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2334.62 | 1636.4 | 1702.506 | 66.106 | 70.1 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2383.84 | 1631.59 | 1702.3999 | 70.8099 | 74.91 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2434.05 | 1627.87 | 1702.2917 | 74.4217 | 78.63 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2484.14 | 1624.84 | 1702.1838 | 77.3438 | 81.66 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2534.24 | 1621.71 | 1702.0758 | 80.3658 | 84.79 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2584.56 | 1616.07 | 1701.9674 | 85.8974 | 90.43 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2634.69 | 1612.35 | 1701.8593 | 89.5093 | 94.15 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2684.95 | 1607.33 | 1701.751 | 94.421 | 99.17 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2734.2 | 1604.74 | 1701.6449 | 96.9049 | 101.76 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2776.26 | 1604.16 | 1701.5542 | 97.3942 | 102.34 | 16 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2820.55 | 1603.61 | 1701.4588 | 97.8488 | 102.89 | 16 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2870.57 | 1604.97 | 1701.351 | 96.381 | 101.53 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2918.7 | 1605.32 | 1701.2472 | 95.9272 | 101.18 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 2968.7 | 1605.34 | 1701.1395 | 95.7995 | 101.16 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3018.7 | 1605.76 | 1701.0317 | 95.2717 | 100.74 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3068.76 | 1608.15 | 1700.9239 | 92.7739 | 98.35 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3118.24 | 1608.93 | 1700.8172 | 91.8872 | 97.57 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3168.43 | 1609.98 | 1700.7091 | 90.7291 | 96.52 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3218.43 | 1610.25 | 1700.6013 | 90.3513 | 96.25 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3267.65 | 1606.08 | 1700.4952 | 94.4152 | 100.42 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3317.79 | 1602.44 | 1700.3872 | 97.9472 | 104.06 | 16 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3365.71 | 1605.73 | 1700.2839 | 94.5539 | 100.77 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3415.85 | 1609.46 | 1700.1758 | 90.7158 | 97.04 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3466.25 | 1612.49 | 1700.0672 | 87.5772 | 94.01 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3516.25 | 1612.39 | 1699.9595 | 87.5695 | 94.11 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3566.25 | 1612.16 | 1699.8517 | 87.6917 | 94.34 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3613.63 | 1611.42 | 1699.7496 | 88.3296 | 95.08 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3656.26 | 1617.61 | 1699.6577 | 82.0477 | 88.89 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3703.37 | 1623.84 | 1699.5562 | 75.7162 | 82.66 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3742.55 | 1627.29 | 1699.4718 | 72.1818 | 79.21 | 10 | 16
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3792.59 | 1632.94 | 1699.3639 | 66.4239 | 73.56 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3842.83 | 1635.55 | 1699.2557 | 63.7057 | 70.95 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3879.56 | 1639.36 | 1699.1765 | 59.8165 | 67.14 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3929.46 | 1644.25 | 1699.069 | 54.819 | 62.25 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 3978.69 | 1650.98 | 1698.9629 | 47.9829 | 55.52 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 4024.59 | 1656.61 | 1698.8639 | 42.2539 | 49.89 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 4075.79 | 1667.61 | 1698.7536 | 31.1436 | 38.89 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 4126.78 | 1675.63 | 1698.6437 | 23.0137 | 30.87 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 4169.11 | 1678.18 | 1698.5525 | 20.3725 | 28.32 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 4217.54 | 1683.42 | 1698.4481 | 15.0281 | 23.08 | 10 | 10
IPITO_BRANCH | J-003N | IPITO_GSR02 | 4220.82 | 1683.37 | 1698.441 | 15.071 | 23.13 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 0 | 1698.14 | 1697.6 | -0.54 | 4.16 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 97.19 | 1697.85 | 1696.9564 | -0.8936 | 4.45 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 139.33 | 1697.65 | 1696.6774 | -0.97265 | 4.65 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 159.33 | 1697.92 | 1696.5449 | -1.3751 | 4.38 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 179.34 | 1698.32 | 1696.4124 | -1.9076 | 3.98 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 252.76 | 1696.44 | 1695.9262 | -0.51379 | 5.86 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 367.16 | 1689.96 | 1695.1687 | 5.2087 | 12.34 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 416.63 | 1687.09 | 1694.8411 | 7.7511 | 15.21 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 466.72 | 1684.06 | 1694.5094 | 10.4494 | 18.24 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 516.78 | 1681.65 | 1694.1779 | 12.5279 | 20.65 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 566.37 | 1678.51 | 1693.8495 | 15.3395 | 23.79 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 616.45 | 1675.56 | 1693.5178 | 17.9578 | 26.74 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 666.25 | 1673.16 | 1693.1881 | 20.0281 | 29.14 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 716.37 | 1669.72 | 1692.8562 | 23.1362 | 32.58 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 765.46 | 1667.75 | 1692.5311 | 24.7811 | 34.55 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 815.3 | 1664.71 | 1692.2011 | 27.4911 | 37.59 | 10 | 10
UHURU_J004N | UHURU_PARK_GBR | J-004N | 865 | 1661.88 | 1691.8719 | 29.9919 | 40.42 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 915.09 | 1658.92 | 1691.5402 | 32.6202 | 43.38 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 964.33 | 1655.65 | 1691.2142 | 35.5642 | 46.65 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1014.44 | 1652.32 | 1690.8823 | 38.5623 | 49.98 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1064.64 | 1648.96 | 1690.5499 | 41.5899 | 53.34 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1114.74 | 1645.77 | 1690.2181 | 44.4481 | 56.53 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1165.13 | 1643.35 | 1689.8845 | 46.5345 | 58.95 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1215.41 | 1640.12 | 1689.5515 | 49.4315 | 62.18 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1265.59 | 1638.66 | 1689.2192 | 50.5592 | 63.64 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1315.31 | 1636.72 | 1688.89 | 52.17 | 65.58 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1365.32 | 1635.33 | 1688.5588 | 53.2288 | 66.97 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1415.09 | 1634.17 | 1688.2292 | 54.0592 | 68.13 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1464.04 | 1633.32 | 1687.9051 | 54.5851 | 68.98 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1514.49 | 1632.73 | 1687.571 | 54.841 | 69.57 | 10 | 16
UHURU_J004N | UHURU_PARK_GBR | J-004N | 1563.45 | 1628.88 | 1687.2468 | 58.3668 | 73.42 | 10 | 16
MAKAMBINI_BRANCH | J-004N | MAKAMBINI_GSR03 | 0 | 1628.88 | 1687.2468 | 58.3668 | 73.42 | 10 | 16
MAKAMBINI_BRANCH | J-004N | MAKAMBINI_GSR03 | 494 | 1654.5 | 1680.7178 | 26.2178 | 47.8 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 0 | 1628.88 | 1687.2468 | 58.3668 | 73.42 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 50.01 | 1627.73 | 1686.5858 | 58.8558 | 74.57 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 99.84 | 1626.02 | 1685.9272 | 59.9072 | 76.28 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 149.86 | 1624.83 | 1685.2661 | 60.4361 | 77.47 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 199.89 | 1624.86 | 1684.6049 | 59.7449 | 77.44 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 250.23 | 1624.06 | 1683.9396 | 59.8796 | 78.24 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 300.54 | 1620.48 | 1683.2747 | 62.7947 | 81.82 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 350.54 | 1618.66 | 1682.6138 | 63.9538 | 83.64 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 400.8 | 1615.52 | 1681.9496 | 66.4296 | 86.78 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 451.07 | 1612.41 | 1681.2852 | 68.8752 | 89.89 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 501.19 | 1608.98 | 1680.6228 | 71.6428 | 93.32 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 550.84 | 1605.17 | 1679.9666 | 74.7966 | 97.13 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 599.18 | 1601.44 | 1679.3277 | 77.8877 | 100.86 | 10 | 16
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 646.43 | 1598.62 | 1678.7032 | 80.0832 | 103.68 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 696.82 | 1594.67 | 1678.0372 | 83.3672 | 107.63 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 746.46 | 1591.26 | 1677.3811 | 86.1211 | 111.04 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 795.94 | 1589.25 | 1676.7272 | 87.4772 | 113.05 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 845.96 | 1585.71 | 1676.0661 | 90.3561 | 116.59 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 895.93 | 1582.83 | 1675.4056 | 92.5756 | 119.47 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 946 | 1580.25 | 1674.7439 | 94.4939 | 122.05 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 994.92 | 1576.82 | 1674.0973 | 97.2773 | 125.48 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1044.57 | 1574.78 | 1673.4411 | 98.6611 | 127.52 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1093.79 | 1570.33 | 1672.7906 | 102.4606 | 131.97 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1143.99 | 1566.99 | 1672.1271 | 105.1371 | 135.31 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1193.67 | 1564.39 | 1671.4705 | 107.0805 | 137.91 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1243.61 | 1563.42 | 1670.8105 | 107.3905 | 138.88 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1293.64 | 1561.87 | 1670.1493 | 108.2793 | 140.43 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1343.66 | 1561.37 | 1669.4882 | 108.1182 | 140.93 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1393.66 | 1561.36 | 1668.8274 | 107.4674 | 140.94 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1443.7 | 1560.78 | 1668.166 | 107.386 | 141.52 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1493.71 | 1561.75 | 1667.505 | 105.755 | 140.55 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1542.68 | 1561.68 | 1666.8578 | 105.1778 | 140.62 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1593.05 | 1562.29 | 1666.1921 | 103.9021 | 140.01 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1643.07 | 1560.95 | 1665.531 | 104.581 | 141.35 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1693.14 | 1560.23 | 1664.8693 | 104.6393 | 142.07 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1743.15 | 1561.13 | 1664.2083 | 103.0783 | 141.17 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1792.17 | 1562.71 | 1663.5604 | 100.8504 | 139.59 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1841.45 | 1562.97 | 1662.9091 | 99.9391 | 139.33 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1891.2 | 1561.24 | 1662.2516 | 101.0116 | 141.06 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1941.32 | 1559.55 | 1661.5892 | 102.0392 | 142.75 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 1991.39 | 1556.87 | 1660.9274 | 104.0574 | 145.43 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2041.61 | 1552.24 | 1660.2637 | 108.0237 | 150.06 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2090.78 | 1551.19 | 1659.6138 | 108.4238 | 151.11 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2139.77 | 1552 | 1658.9663 | 106.9663 | 150.3 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2189.78 | 1552.84 | 1658.3054 | 105.4654 | 149.46 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2240.02 | 1557.74 | 1657.6414 | 99.9014 | 144.56 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2290.05 | 1559.56 | 1656.9801 | 97.4201 | 142.74 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2340.06 | 1559.01 | 1656.3192 | 97.3092 | 143.29 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2389.69 | 1556.47 | 1655.6632 | 99.1932 | 145.83 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2439.8 | 1553.12 | 1655.001 | 101.881 | 149.18 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2489.66 | 1550.81 | 1654.342 | 103.532 | 151.49 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2538.5 | 1545.15 | 1653.6965 | 108.5465 | 157.15 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2586.9 | 1541.47 | 1653.0568 | 111.5868 | 160.83 | 16 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2637.44 | 1534.83 | 1652.3888 | 117.5588 | 167.47 | 25 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2687.71 | 1529.68 | 1651.7244 | 122.0444 | 172.62 | 25 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2737.56 | 1524.17 | 1651.0656 | 126.8956 | 178.13 | 25 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2781.84 | 1522.73 | 1650.4804 | 127.7504 | 179.57 | 25 | 25
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | 2790.5 | 1522.61 | 1650.3659 | 127.7559 | 179.69 | 25 | 25

## ER comparison - links
Link | ER description | ER length (m) | Alignment plan length (m) | Model length incl. slope (m) | Difference vs ER (m) | Design Q (m3/day) | Hours/day | V (m/s)
ABSTRACTION | Abstraction pipe STEEL DN600-PN10, L = 100 m | 100 |  | 100 | 0 | 21505.3763 | 22 | 0.96035
LL_DELIVERY | ASSUMED short delivery pipe low-lift PS -> grit tank |  |  | 30 |  | 21505.3763 | 22 | 0.96035
RAW_MAIN | Raw water pipe STEEL DN600-PN10, L = 1,177 m, V = 0.97 m/s | 1177 | 1078.37 | 1078.46 | -98.54 | 21505.3763 | 22 | 0.96035
WTP_IKANA_RM | Rising main STEEL DN600 PN10/16/25/30/40, L = 20,994 m, V = 0.9 m/s | 20994 | 19638.7081 | 19665.64 | -1328.36 | 20000 | 22 | 0.89313
IKANA_NKANGAMO_GM | Gravity main STEEL DN600 PN10/16/25, L = 38,504 m, V = 0.82 m/s | 38504 | 38877.072 | 38930.17 | 426.17 | 20000 | 24 | 0.8187
BPS_RM_1 | Rising main STEEL DN600 PN10/16/25, L = 21,673 m (BPS -> Uhuru Park), V = 0.9 m/s | 21673 | 19563.398 | 19581.43 | -2091.57 | 20000 | 22 | 0.89313
BPS_RM_2 |  |  | 40 | 40.02 |  | 19628.48 | 22 | 0.87653
BPS_RM_3 |  |  | 100.25 | 100.25 |  | 18081.92 | 22 | 0.80747
UHURU_INLET | ASSUMED 50 m from J-003N to the Uhuru Park GBR inlet |  |  | 50 |  | 17459.82 | 22 | 0.77969
ESR_BRANCH | STEEL DN100-PN10, L = 38 m (schematic label DN80) | 38 |  | 38 | 0 | 371.52 | 22 | 0.59727
GSR01_BRANCH | STEEL DN150-PN16, L = 40 m | 40 |  | 40 | 0 | 1546.56 | 22 | 1.105
IPITO_BRANCH | STEEL DN150-PN10, L = 4,285 m | 4285 | 4211.6595 | 4220.82 | -64.18 | 622.1 | 22 | 0.44449
UHURU_J004N | Gravity STEEL DN150-PN10, L = 1,555 m, Q = 1,244.2 m3/day | 1555 | 1561.49 | 1563.45 | 8.45 | 1244.2 | 24 | 0.8149
MAKAMBINI_BRANCH | STEEL DN100-PN10, L = 494 m (route not surveyed - straight line) | 494 |  | 494 | 0 | 622.1 | 24 | 0.91676
CHAPWA_BRANCH | STEEL DN100-PN25, L = 2,664 m | 2664 | 2785.97 | 2790.5 | 126.5 | 622.1 | 24 | 0.91676

## ER comparison - pumps
Station | Pumps | ER Q/pump (m3/h) | Model Q/pump (m3/h) | ER head (m) | Model TDH (m) | Head difference (m) | Model shaft kW/pump | Model motor kW/pump
MOMBA_INTAKE | 1W+1S | 978 | 977.5171 | 10 | 12.0535 | 2.0535 | 42.8096 | 55
GRIT_TANK | 1W+1S | 978 | 977.5171 | 25 | 17.4215 | -7.5785 | 61.8751 | 75
MOMBA_WTP | 3W+1S | 304 | 303.0303 | 330 | 334.1325 | 4.1325 | 353.7339 | 450
NKANGAMO_BPS | 2W+1S | 455 | 454.5455 | 221 | 188.2284 | -32.7716 | 298.9059 | 355

## ER comparison - PN
Link | Basis | PN10 | PN16 | PN25 | PN30 | PN40 | PN64 | > max
ABSTRACTION | ER | 100
ABSTRACTION | model working | 100
ABSTRACTION | model + surge | 100
RAW_MAIN | ER | 1177
RAW_MAIN | model working | 1078.46
RAW_MAIN | model + surge | 1078.46
WTP_IKANA_RM | ER | 305 | 119 | 4705 | 10798 | 5067
WTP_IKANA_RM | model working | 257.34 | 435.6 | 6745.88 | 10776.5 | 1450.32
WTP_IKANA_RM | model + surge | 257.34 |  | 1981.12 | 11500.86 | 5926.32
IKANA_NKANGAMO_GM | ER | 2877 | 13247 | 22380
IKANA_NKANGAMO_GM | model working | 570.33 | 18575.42 | 19784.42
IKANA_NKANGAMO_GM | model + surge |  | 2370.56 | 36559.61
BPS_RM_1 | ER | 10310 | 7177 | 4185
BPS_RM_1 | model working | 12023.1 | 5623.74 | 1934.59
BPS_RM_1 | model + surge | 6458.65 | 5604.62 | 7518.16
ESR_BRANCH | ER | 38
ESR_BRANCH | model working | 38
ESR_BRANCH | model + surge | 38
GSR01_BRANCH | ER |  | 40
GSR01_BRANCH | model working | 40
GSR01_BRANCH | model + surge |  | 40
IPITO_BRANCH | ER | 4285
IPITO_BRANCH | model working | 3986.39 | 234.43
IPITO_BRANCH | model + surge | 2812.07 | 1408.75
UHURU_J004N | ER | 1555
UHURU_J004N | model working | 1563.45
UHURU_J004N | model + surge | 815.3 | 748.15
MAKAMBINI_BRANCH | ER | 494
MAKAMBINI_BRANCH | model working | 494
MAKAMBINI_BRANCH | model + surge |  | 494
CHAPWA_BRANCH | ER |  |  | 2664
CHAPWA_BRANCH | model working | 599.18 | 1987.72 | 203.6
CHAPWA_BRANCH | model + surge |  | 599.18 | 2191.32

## EPANET ER_pumps stations
Station | Duty pumps | EPANET Q/pump (l/s) | Design Q/pump (l/s) | ER Q/pump (l/s) | EPANET Q total (m3/h) | Design Q total (m3/h) | EPANET pump head (m) | Design TDH (m) | ER head (m) | Flow vs design (%)
MOMBA_INTAKE | 1 | 295.748 | 271.5325 | 271.6667 | 1064.6926 | 977.5171 | 9.384 | 12.0535 | 10 | 8.9181
GRIT_TANK | 1 | 341.7547 | 271.5325 | 271.6667 | 1230.3168 | 977.5171 | 20.1486 | 17.4215 | 25 | 25.8614
MOMBA_WTP | 3 | 83.4731 | 84.1751 | 84.4444 | 901.5098 | 909.0909 | 332.5048 | 334.1325 | 330 | -0.83391
NKANGAMO_BPS | 2 | 126.2627 | 126.2626 | 126.3889 | 909.0912 | 909.0909 | 221.1483 | 188.2284 | 221 | 4.7684e-05

## EPANET ER_pumps links
Link | EPANET Q (l/s) | Design Q (l/s) | Flow diff (%) | EPANET Pmin along route (m) | EPANET Pmax along route (m) | EPANET HGL at end (m) | Design HGL at end (m) | FCV status
ABSTRACTION | 295.7479 | 271.5325 | 8.918 |  |  | 1360.7914 | 1360.8218
LL_DELIVERY | 295.7479 | 271.5325 | 8.918 |  |  | 1366.5499 | 1369
RAW_MAIN | 341.7546 | 271.5325 | 25.8614 | 7.2064 | 15.7167 | 1379 | 1379
WTP_IKANA_RM | 250.4191 | 252.5253 | -0.83403 | 6.6208 | 324.8144 | 1667.95 | 1669
IKANA_NKANGAMO_GM | 231.4811 | 231.4815 | -0.00017285 | 69.0783 | 209.3693 | 1616.3517 | 1611.685 | ACTIVE (controlling)
BPS_RM_1 | 252.5251 | 252.5253 | -4.1723e-05 | 38.4468 | 209.3163 | 1740.7037 | 1707.7271
BPS_RM_2 | 247.8341 | 247.8343 | -8.9407e-05 | 41.4937 | 41.4937 | 1740.6436 | 1707.6669
BPS_RM_3 | 228.3071 | 228.3071 | 1.1921e-05 | 41.0177 | 41.1615 | 1740.5142 | 1707.5374
UHURU_INLET | 220.4521 | 220.4523 | -9.5367e-05 |  |  | 1740.4535 | 1707.4768 | ACTIVE (controlling)
ESR_BRANCH | 4.691 | 4.6909 | 0.0026226 |  |  | 1740.4764 | 1707.5 | ACTIVE (controlling)
GSR01_BRANCH | 19.527 | 19.5273 | -0.00121 |  |  | 1740.1777 | 1707.2013 | ACTIVE (controlling)
IPITO_BRANCH | 7.855 | 7.8548 | 0.0031471 | 40.7514 | 129.7198 | 1731.4125 | 1698.441 | ACTIVE (controlling)
UHURU_J004N | 14.4001 | 14.4005 | -0.0022054 | 1.5419 | 58.2864 | 1691.892 | 1687.2468
MAKAMBINI_BRANCH | 7.2 | 7.2002 | -0.002867 |  |  | 1685.3584 | 1680.7178 | ACTIVE (controlling)
CHAPWA_BRANCH | 7.2001 | 7.2002 | -0.0015318 | 62.3006 | 131.1687 | 1654.9841 | 1650.3659 | ACTIVE (controlling)

## EPANET design_pumps stations
Station | Duty pumps | EPANET Q/pump (l/s) | Design Q/pump (l/s) | ER Q/pump (l/s) | EPANET Q total (m3/h) | Design Q total (m3/h) | EPANET pump head (m) | Design TDH (m) | ER head (m) | Flow vs design (%)
MOMBA_INTAKE | 1 | 327.1842 | 271.5325 | 271.6667 | 1177.863 | 977.5171 | 10.2369 | 12.0535 | 10 | 20.4954
GRIT_TANK | 1 | 272.1163 | 271.5325 | 271.6667 | 979.6187 | 977.5171 | 17.3955 | 17.4215 | 25 | 0.21499
MOMBA_WTP | 3 | 84.5039 | 84.1751 | 84.4444 | 912.6423 | 909.0909 | 333.2712 | 334.1325 | 330 | 0.39066
NKANGAMO_BPS | 2 | 126.2626 | 126.2626 | 126.3889 | 909.0907 | 909.0909 | 188.2274 | 188.2284 | 221 | -1.1921e-05

## EPANET design_pumps links
Link | EPANET Q (l/s) | Design Q (l/s) | Flow diff (%) | EPANET Pmin along route (m) | EPANET Pmax along route (m) | EPANET HGL at end (m) | Design HGL at end (m) | FCV status
ABSTRACTION | 327.1842 | 271.5325 | 20.4954 |  |  | 1360.7485 | 1360.8218
LL_DELIVERY | 327.1842 | 271.5325 | 20.4954 |  |  | 1366.5499 | 1369
RAW_MAIN | 272.1163 | 271.5325 | 0.21499 | 7.1064 | 14.8262 | 1379 | 1379
WTP_IKANA_RM | 253.5114 | 252.5253 | 0.39053 | 6.6214 | 325.5059 | 1667.95 | 1669
IKANA_NKANGAMO_GM | 231.4811 | 231.4815 | -0.00017285 | 69.0783 | 209.3693 | 1616.3517 | 1611.685 | ACTIVE (controlling)
BPS_RM_1 | 252.525 | 252.5253 | -8.9407e-05 | 5.5259 | 176.3954 | 1707.783 | 1707.7271
BPS_RM_2 | 247.834 | 247.8343 | -0.00012517 | 8.5727 | 8.5727 | 1707.7227 | 1707.6669
BPS_RM_3 | 228.307 | 228.3071 | -1.1921e-05 | 8.0969 | 8.2407 | 1707.5931 | 1707.5374
UHURU_INLET | 220.452 | 220.4523 | -0.00011921 |  |  | 1707.5326 | 1707.4768 | ACTIVE (controlling)
ESR_BRANCH | 4.691 | 4.6909 | 0.001967 |  |  | 1707.5555 | 1707.5 | ACTIVE (controlling)
GSR01_BRANCH | 19.527 | 19.5273 | -0.0013769 |  |  | 1707.2568 | 1707.2013 | ACTIVE (controlling)
IPITO_BRANCH | 7.855 | 7.8548 | 0.0027418 | 7.8305 | 96.7989 | 1698.4917 | 1698.441 | ACTIVE (controlling)
UHURU_J004N | 14.4001 | 14.4005 | -0.0022054 | 1.5419 | 58.2864 | 1691.892 | 1687.2468
MAKAMBINI_BRANCH | 7.2 | 7.2002 | -0.002867 |  |  | 1685.3584 | 1680.7178 | ACTIVE (controlling)
CHAPWA_BRANCH | 7.2001 | 7.2002 | -0.0015318 | 62.3006 | 131.1687 | 1654.9841 | 1650.3659 | ACTIVE (controlling)

## Warnings
Item | Warning / design note
UHURU_PARK_GBR | gravity zone from Uhuru Park GBR 5,000 m3 (Tunduma) is short of head by 3.9 m - increase pipe sizes (or set dn 'auto') or add a booster pump
RAW_MAIN | pump trip / valve closure can drop pressure to -90 m (surge 98 m) - surge protection needed (surge vessel, air valves)
WTP_IKANA_RM | pump trip / valve closure can drop pressure to -82 m (surge 91 m) - surge protection needed (surge vessel, air valves)
IKANA_NKANGAMO_GM | pump trip / valve closure can drop pressure to -18 m (surge 83 m) - surge protection needed (surge vessel, air valves)
BPS_RM_1 | pump trip / valve closure can drop pressure to -84 m (surge 91 m) - surge protection needed (surge vessel, air valves)
IPITO_BRANCH | pump trip / valve closure can drop pressure to -36 m (surge 45 m) - surge protection needed (surge vessel, air valves)
UHURU_J004N | negative pressure -1.9 m along the pipe - HGL below ground
UHURU_J004N | pump trip / valve closure can drop pressure to -85 m (surge 83 m) - surge protection needed (surge vessel, air valves)
CHAPWA_BRANCH | pump trip / valve closure can drop pressure to -35 m (surge 93 m) - surge protection needed (surge vessel, air valves)
MAKAMBINI_BRANCH | pump trip / valve closure can drop pressure to -35 m (surge 93 m) - surge protection needed (surge vessel, air valves)
NKANGAMO_BPS | arrives with 53.2 m excess head - fit a flow control valve / PRV at the inlet or reduce the pipe size
IPITO_GSR02 | arrives with 13.2 m excess head - fit a flow control valve at the inlet
MAKAMBINI_GSR03 | arrives with 21.0 m excess head - fit a flow control valve / PRV at the inlet or reduce the pipe size
CHAPWA_GSR04 | arrives with 125.0 m excess head - fit a flow control valve / PRV at the inlet or reduce the pipe size