## Read Me
Tunduma Water Supply – Zone Calculator
Hydraulic analysis from the Momba River intake to the Tunduma tanks, split by zone. Every result is a live Excel formula.
WHEN YOU RECEIVE THE REAL LEVELS – 4 STEPS
Step 1 – sheet 'Levels' | type ground, floor, MINIMUM and MAXIMUM water level, inlet level and capacity of every tank / sump / river. Read the 'Check' column: it must say OK.
Step 2 – sheet 'Demands' | type the daily demand of each tank and the WTP losses (if they changed).
Step 3 – zone sheets Z1 … Z7 | only if pipes or pumps changed: DN, length, C, hours, number of pumps, efficiencies, ER duty (blue cells).
Step 4 – sheet 'Summary' | read the pump heads (at minimum and maximum suction level), gravity surplus, tank results and storage. Each zone sheet explains its result in section F.
Optional – Python and PDFs | run 'python levels_from_excel.py results/Tunduma_Zone_Calculator.xlsx' to copy the levels into tunduma_config.json, then 'python run_analysis.py' and the PDF scripts to regenerate every report with the same levels.
COLOUR LEGEND
Blue text, yellow fill | input – edit these
Black text | formula – do not overwrite
Green text | link from another sheet
Green fill, bold | key result
WHY MINIMUM AND MAXIMUM LEVELS MATTER
Pumped zone, design case | suction tank at its MINIMUM level → the pump must lift the most → TDH max (used to size pump and motor).
Pumped zone, low-head case | suction tank at its MAXIMUM level → least lift → TDH min (the pump must also run safely here: it gives more flow unless throttled / VFD).
Gravity zone, design case | supplying tank at its MINIMUM level → least energy available → must still reach every tank (surplus ≥ 0).
Gravity zone, high case | supplying tank at its MAXIMUM level → most energy → the valve must burn the biggest surplus; static pressure (pipe class) uses this level.
Receiving tank | water must arrive at the inlet level (or the maximum level if the inlet is lower / submerged) plus a small residual head.
ZONES (split at every free water surface)
Z1 River-Intake | gravity: Momba River → intake sump (abstraction pipe)
Z2 Intake-Grit | pumped: low-lift pumps, intake sump → grit tank
Z3 Grit-WTP | pumped: high-lift pumps, grit tank → WTP inlet (raw-water main)
Z4 WTP-Ikana | pumped: WTP clear-water pumps → Ikana GBR (treated-water rising main)
Z5 Ikana-Nkangamo | gravity: Ikana GBR → Nkangamo BPS sump
Z6 Nkangamo-Uhuru | pumped: Nkangamo BPS → J-001N (ESR), J-002N (GSR01), J-003N (Ipito) → Uhuru Park GBR
Z7 Uhuru-Chapwa | gravity: Uhuru Park GBR → J-004N → Makambini GSR03 and Chapwa GSR04
METHOD (Bernoulli / energy equation between two water surfaces)
z1 + p1/ρg + V1²/2g + Hp = z2 + p2/ρg + V2²/2g + hL | at tank surfaces p = 0 and V ≈ 0
Pumped zone | Hp = H_req − z1 ; TDH = Hp + station losses
Gravity zone | surplus = z1 − H_req (≥ 0 OK, burnt by an FCV/PRV; < 0 short of head)
H_req (head needed at zone start) | largest of: each destination arrival level + residual + losses on the way, and each critical point crown + min. pressure + losses up to it
Friction (Hazen-Williams) | hf = 10.67 L Q^1.852 / (C^1.852 D^4.8704) ; hL = hf × (1 + minor-loss factor)
Pressure at a point | p = HGL − pipe crown ; working = max(p, static level − crown) ; PN = smallest class ≥ working × 0.0981 bar/m
Surge (Joukowsky) | Δh = a V / g
SOURCE OF THE STARTING VALUES
Employer's Requirements | flows, pipe sizes and lengths, pump duties, tank elevations and capacities.
ASSUMED (to confirm) | operating water levels, inlet levels, WTP inlet, C value, station losses, pipe cover – marked in 'Levels' column M and in cell notes.
Check | column 'Python model' on Summary = run_analysis.py with the starting inputs.

## Levels
Levels of every water surface – ENTER THE REAL LEVELS HERE
Minimum and maximum water levels drive every zone. Blank inlet = the maximum level is used. All levels in m above datum (survey datum).
ID | Facility | Role | Ground level (m) | Floor level (m) | MINIMUM water level (m) | MAXIMUM water level (m) | Inlet level (m) | Capacity (m³) | Water depth (m) | Plan area (m²) | Arrival level used (m) | Source / status | Check
MOMBA_RIVER | Momba (Saisi) River | source: minimum = dry-season low level, maximum = flood level | 1363 |  | 1361 | 1364.5 |  |  |  |  | 1364.5 | levels ASSUMED – confirm | OK
MOMBA_INTAKE | Momba Intake - low lift PS | intake sump: minimum = pump start/stop low level (submergence) | 1365.94 |  | 1360 | 1364 |  |  |  |  | 1360 | ER elevation/capacity; levels ASSUMED – confirm | OK
GRIT_TANK | Grit tank - high lift PS | grit tank = high-lift pump suction; receives low-lift flow | 1365.94 |  | 1366.5 | 1368 | 1368 |  |  |  | 1368 | ER elevation/capacity; levels ASSUMED – confirm | OK
MOMBA_WTP | Momba WTP (20,000 m3/day) | inlet = aerator inlet; min/max/capacity = CLEAR-WATER tank (pump suction) | 1372.1 | 1368 | 1368.5 | 1373 | 1378 | 4000 | 5 | 800 | 1378 | ER elevation/capacity; levels ASSUMED – confirm | OK
IKANA_GBR | Ikana (Momba) GBR 3,000 m3 | receives WTP pumping; supplies gravity main | 1663 | 1663 | 1663.3 | 1668 |  | 3000 | 5 | 600 | 1668 | ER elevation/capacity; levels ASSUMED – confirm | OK
NKANGAMO_BPS | Nkangamo BPS | BPS sump: receives gravity main; BPS pump suction | 1555.5 | 1552.5 | 1553 | 1557 | 1557.5 | 2000 | 4.5 | 444.4444 | 1557.5 | ER elevation/capacity; levels ASSUMED – confirm | OK
UHURU_PARK_GBR | Uhuru Park GBR 5,000 m3 (Tunduma) | receives BPS main; supplies town + J-004N | 1697.3 | 1697.3 | 1697.6 | 1702.3 |  | 5000 | 5 | 1000 | 1702.3 | ER elevation/capacity; levels ASSUMED – confirm | OK
TUNDUMA_ESR | Existing Tunduma ESR 120 m3 | existing elevated tank (from J-001N) | 1700 | 1703.5 | 1703.5 | 1706.5 |  | 120 | 3 | 40 | 1706.5 | ER elevation/capacity; levels ASSUMED – confirm | OK
UHURU_GSR01 | Existing Tunduma Uhuru GSR 01 500 m3 | existing tank (from J-002N) | 1698.4 | 1698.4 | 1698.4 | 1701.4 |  | 500 | 3 | 166.6667 | 1701.4 | ER elevation/capacity; levels ASSUMED – confirm | OK
IPITO_GSR02 | Existing Tunduma Ipito GSR 02 | existing tank (from J-003N) | 1681.2 | 1681.2 | 1681.2 | 1684.2 |  | 200 | 3 | 66.6667 | 1684.2 | ER elevation/capacity; levels ASSUMED – confirm | OK
MAKAMBINI_GSR03 | Existing Tunduma Makambini GSR 03 | existing tank (from J-004N, gravity) | 1655.7 | 1655.7 | 1655.7 | 1658.7 |  | 200 | 3 | 66.6667 | 1658.7 | ER | OK
CHAPWA_GSR04 | Existing Tunduma Chapwa GSR 04 | existing tank (from J-004N, gravity) | 1521.4 | 1521.4 | 1521.4 | 1524.4 |  | 200 | 3 | 66.6667 | 1524.4 | ER | OK
Notes
MINIMUM level = lowest operating level (pump cut-out / bottom water level, BWL). MAXIMUM level = top water level (TWL, overflow level).
Floor and capacity are used for the depth/area check and the Storage sheet; they do not change the hydraulics.
If the real inlet is a free fall above the tank, enter its level in 'Inlet level'; if it enters from below, leave it blank.
After typing new levels, look at Summary – every zone, tank and pressure check updates.
Note on L5: Water must reach the inlet; if the inlet is below the maximum level (submerged) the maximum level counts.
Note on L6: Intake: water enters below the surface, so the sump MINIMUM level is what the river must hold.
Note on L7: Water must reach the inlet; if the inlet is below the maximum level (submerged) the maximum level counts.
Note on L8: WTP: raw water must reach the aerator inlet (column H); min/max are the clear-water tank.
Note on L9: Water must reach the inlet; if the inlet is below the maximum level (submerged) the maximum level counts.
Note on L10: Water must reach the inlet; if the inlet is below the maximum level (submerged) the maximum level counts.
Note on L11: Water must reach the inlet; if the inlet is below the maximum level (submerged) the maximum level counts.
Note on L12: Water must reach the inlet; if the inlet is below the maximum level (submerged) the maximum level counts.
Note on L13: Water must reach the inlet; if the inlet is below the maximum level (submerged) the maximum level counts.
Note on L14: Water must reach the inlet; if the inlet is below the maximum level (submerged) the maximum level counts.
Note on L15: Water must reach the inlet; if the inlet is below the maximum level (submerged) the maximum level counts.
Note on L16: Water must reach the inlet; if the inlet is below the maximum level (submerged) the maximum level counts.

## Summary
Summary of all zones
Linked to the zone sheets (green). Change levels on 'Levels' and read the result here. 'Python model' = run_analysis.py with the starting inputs.
Zones
Zone | Type | Flow (l/s) | Velocity first pipe (m/s) | hL first pipe (m) | H_req (m a.s.l.) | Set by | Design: TDH (m) / surplus (m) | Start at MAX level: TDH (m) / surplus (m) | ER duty head (m) | TDH − ER (m) | Shaft kW per pump | Motor kW per pump | Energy (kWh/d) | Lowest pressure on route (m) | Python model (m) | Excel − Python (m)
Z1 River-Intake | gravity | 271.5325 | 0.96035 | 0.17817 | 1360.1782 | MOMBA_INTAKE | 0.82183 | 4.3218 | – | – | – | – | – | no points between tanks | 0.82 | 0.0018263
Z2 Intake-Grit | pumped | 271.5325 | 0.96035 | 0.053452 | 1369.0535 | GRIT_TANK | 12.0535 | 8.0535 | 10 | 2.0535 | 42.8096 | 55 | 1001.9265 | no points between tanks | 12.05 | 0.0034521
Z3 Grit-WTP | pumped | 271.5325 | 0.96035 | 1.9216 | 1380.9216 | MOMBA_WTP | 17.4216 | 15.9216 | 25 | -7.5784 | 61.8754 | 75 | 1448.1467 | 8.3046 | 17.42 | 0.0016037
Z4 WTP-Ikana | pumped | 252.5253 | 0.89313 | 30.6324 | 1699.6324 | IKANA_GBR | 334.1324 | 329.6324 | 330 | 4.1324 | 353.7338 | 450 | 24575.1915 | 8.8711 | 334.13 | 0.0024197
Z5 Ikana-Nkangamo | gravity | 231.4815 | 0.8187 | 51.615 | 1610.115 | NKANGAMO_BPS | 53.185 | 57.885 | – | – | – | – | – | 65.6117 | 53.18 | 0.0049535
Z6 Nkangamo-Uhuru | pumped | 252.5253 | 0.89313 | 30.5013 | 1738.2284 | TUNDUMA_ESR | 188.2284 | 184.2284 | 221 | -32.7716 | 298.9058 | 355 | 13844.0583 | 6.6727 | 188.23 | -0.0016106
Z7 Uhuru-Chapwa | gravity | 14.4005 | 0.8149 | 10.3536 | 1701.5073 | point on UHURU_J004N | -3.9073 | 0.79267 | – | – | – | – | – | -1.9076 | -3.91 | 0.0026683
Total pumping energy | [12 empty] | 40869.3231
Pumped zones: H = pump head with suction at MINIMUM level (design), I = with suction at MAXIMUM level. Gravity zones: H/I = spare head with the supplying tank at MIN/MAX level (≥ 0 OK, burnt by a valve; < 0 short of head).
Tanks and sumps
Tank | MIN level (m) | MAX level (m) | Arrival level (m) | Fed by zone | Arriving HGL (m) | Excess head, design (m) | Excess head, max (m) | Inlet comment | Capacity (m³) | Storage required (m³) | Storage status
MOMBA_INTAKE | 1360 | 1364 | 1360 | Z1 River-Intake | 1360.8218 | 0.82183 | 4.3218 | OK |  | – | –
GRIT_TANK | 1366.5 | 1368 | 1368 | Z2 Intake-Grit | 1369 | 0 | 4 | OK |  | – | –
MOMBA_WTP | 1368.5 | 1373 | 1378 | Z3 Grit-WTP | 1379 | 0 | 1.5 | OK | 4000 | – | –
IKANA_GBR | 1663.3 | 1668 | 1668 | Z4 WTP-Ikana | 1669 | 0 | 4.5 | OK | 3000 | 1666.6667 | OK
NKANGAMO_BPS | 1553 | 1557 | 1557.5 | Z5 Ikana-Nkangamo | 1611.685 | 53.185 | 57.885 | fit flow control valve / PRV (burns 53.2–57.9 m) | 2000 | 1666.6667 | OK
TUNDUMA_ESR | 1703.5 | 1706.5 | 1706.5 | Z6 Nkangamo-Uhuru | 1707.5 | 0 | 4 | OK | 120 | 30.96 | OK
UHURU_GSR01 | 1698.4 | 1701.4 | 1701.4 | Z6 Nkangamo-Uhuru | 1707.2014 | 4.8014 | 8.8014 | fit flow control valve / PRV (burns 4.8–8.8 m) | 500 | 128.88 | OK
IPITO_GSR02 | 1681.2 | 1684.2 | 1684.2 | Z6 Nkangamo-Uhuru | 1698.4412 | 13.2412 | 17.2412 | fit flow control valve / PRV (burns 13.2–17.2 m) | 200 | 51.8417 | OK
UHURU_PARK_GBR | 1697.6 | 1702.3 | 1702.3 | Z6 Nkangamo-Uhuru | 1707.4769 | 4.1769 | 8.1769 | fit flow control valve / PRV (burns 4.2–8.2 m) | 5000 | 1454.985 | OK
MAKAMBINI_GSR03 | 1655.7 | 1658.7 | 1658.7 | Z7 Uhuru-Chapwa | 1680.7175 | 21.0175 | 25.7175 | fit flow control valve / PRV (burns 21.0–25.7 m) | 200 | 0 | OK
CHAPWA_GSR04 | 1521.4 | 1524.4 | 1524.4 | Z7 Uhuru-Chapwa | 1650.3656 | 124.9656 | 129.6656 | fit flow control valve / PRV (burns 125.0–129.7 m) | 200 | 0 | OK
Levels check (from sheet Levels)
All levels entered and consistent
Note on P6: Value from run_analysis.py (Python model) with the starting inputs. Fixed number, for checking.
Note on P7: Value from run_analysis.py (Python model) with the starting inputs. Fixed number, for checking.
Note on P8: Value from run_analysis.py (Python model) with the starting inputs. Fixed number, for checking.
Note on P9: Value from run_analysis.py (Python model) with the starting inputs. Fixed number, for checking.
Note on P10: Value from run_analysis.py (Python model) with the starting inputs. Fixed number, for checking.
Note on P11: Value from run_analysis.py (Python model) with the starting inputs. Fixed number, for checking.
Note on P12: Value from run_analysis.py (Python model) with the starting inputs. Fixed number, for checking.

## Demands
Demands and design flows
Daily volumes (m³/d) supplied by each tank; pipe volumes follow by mass balance.
Tank demands (ER schematic, design year 2035)
Uhuru Park GBR – town supply | 16215.62 | m³/d | ER schematic
Existing Uhuru GSR 01 | 1546.56 | m³/d | ER schematic
Existing Tunduma ESR | 371.52 | m³/d | ER schematic
Existing Ipito GSR 02 | 622.1 | m³/d | ER schematic
Existing Makambini GSR 03 | 622.1 | m³/d | ER schematic
Existing Chapwa GSR 04 | 622.1 | m³/d | ER schematic
WTP + intake-to-WTP losses | 7% | – | ER Table 8: 2 % + 5 %
Daily volume in each pipe (mass balance, downstream → upstream)
J-004N → Makambini | 622.1 | m³/d
J-004N → Chapwa | 622.1 | m³/d
Uhuru Park → J-004N | 1244.2 | m³/d
J-003N → Uhuru Park GBR | 17459.82 | m³/d
J-003N → Ipito | 622.1 | m³/d
J-002N → GSR01 | 1546.56 | m³/d
J-001N → ESR | 371.52 | m³/d
J-002N → J-003N | 18081.92 | m³/d
J-001N → J-002N | 19628.48 | m³/d
Nkangamo BPS → J-001N | 20000 | m³/d
Ikana GBR → Nkangamo BPS | 20000 | m³/d
WTP → Ikana GBR (net WTP output) | 20000 | m³/d
Raw water: intake → WTP | 21505.3763 | m³/d | net ÷ (1 − losses)
Low-lift → grit tank | 21505.3763 | m³/d
River → intake sump | 21505.3763 | m³/d

## Global
Global constants and design criteria
Used by every zone (named cells).
Constants and criteria
Gravitational acceleration g | 9.81 | m/s² | physical constant
Minor losses as fraction of friction | 0.1 | – | ASSUMED 10 % (bends, valves, fittings)
Losses inside each pump station | 3 | m | ASSUMED pipework/valves/meter
Residual head above a tank inlet | 1 | m | ASSUMED safety margin
Pipe crown depth below ground | 1.2 | m | ASSUMED
Minimum pressure at pipe crown along mains | 2 | m | ASSUMED
Minimum pressure at junctions / delivery | 5 | m | ER Table 7
Pressure wave speed a (steel) | 1000 | m/s | ASSUMED, for surge
Motor size margin over shaft power | 1.15 | – | common practice
Electricity tariff | 0 | per kWh | enter the TANESCO tariff
Bar per metre of water | 0.0981 | bar/m | ρg/10⁵
Default Hazen-Williams C | 120 | – | ASSUMED, cement-lined steel (aged)
Excess head above which a flow control valve is flagged | 5 | m | judgement
Pipe pressure classes (PN, bar)
PN10 | 10
PN16 | 16
PN25 | 25
PN30 | 30
PN40 | 40
PN64 | 64
Standard motor sizes (kW)
0.75
1.1
1.5
2.2
3
4
5.5
7.5
11
15
18.5
22
30
37
45
55
75
90
110
132
160
200
250
315
355
400
450
500
560
630
710
800
900
1000
1120
1250
1400
1600
1800
2000
2240
2500
2800
3150
3550
4000
4500
5000
5600
6300

## Z1 River-Intake
Zone 1 – Momba River to intake sump (gravity)
The river fills the intake sump by gravity through the abstraction pipe. The river at its MINIMUM (dry-season) level must stay above the sump MINIMUM level plus the pipe loss, otherwise the low-lift pumps lose submergence.
A. Inputs (levels come from sheet 'Levels')
Start: MOMBA_RIVER MINIMUM water level | 1361 | m a.s.l. | point 1 of Bernoulli, design case (least energy at the start)
Start: MOMBA_RIVER MAXIMUM water level | 1364.5 | m a.s.l. | low-head case for pumps / highest energy for gravity
Operating hours per day | 22 | h/d | carries the intake pump flow while the pumps run
Static level for pressure class | 1364.5 | m a.s.l. | MAXIMUM level of the supplying tank (water at rest)
B. Pipes – flow (continuity) and friction (Hazen-Williams)
Pipe | From | To | Upstream pipe | DN | Internal D (mm) | Length L (m) | C (H-W) | Daily volume (m³/d) | Q (m³/s) | Q (l/s) | Area (m²) | V (m/s) | hf friction (m) | hm minor (m) | hL total (m) | Gradient (m/km) | Loss before this pipe (m) | HGL start (m) | HGL end (m) | Surge Δh = aV/g (m)
ABSTRACTION | MOMBA_RIVER | MOMBA_INTAKE | – | 600 | 600 | 100 | 120 | 21505.3763 | 0.27153 | 271.5325 | 0.28274 | 0.96035 | 0.16198 | 0.016198 | 0.17817 | 1.7817 | 0 | 1361 | 1360.8218 | 97.895
C. Destinations – Bernoulli to each receiving water surface (levels from 'Levels')
Destination | Ends with pipe | MIN level (m) | MAX level (m) | Arrival level (m) | Residual (m) | z2 = arrival + residual (m) | Head needed at zone start = z2 + losses (m) | Arriving HGL, design case (m) | Excess head, design case (m) | Excess head, start at MAX level (m) | Comment
MOMBA_INTAKE | ABSTRACTION | 1360 | 1364 | 1360 | 0 | 1360 | 1360.1782 | 1360.8218 | 0.82183 | 4.3218 | OK
D. Critical points along the pipes – pressure check (add your own rows)
Pipe | Chainage in pipe x (m) | Ground level (m) | Pipe crown (m) | Head needed at zone start (m) | HGL at point (m) | Pressure (m) | Static (m) | Working (m) | Working (bar) | PN required | Transient min = p − Δh (m) | Note | Status
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
E. Bernoulli result
Head needed at zone start H_req | 1360.1782 | m a.s.l. | largest of sections C, C2 (junctions) and D (points)
Set by | MOMBA_INTAKE |  | governing destination, junction or point
Surplus = z1 − H_req (start at MINIMUM level) | 0.82183 | m | design case: must be ≥ 0
Surplus with start at MAXIMUM level | 4.3218 | m | largest head the valve must burn
Status | OK – valve burns 0.8 to 4.3 m
Lowest pressure at any survey point (sheet Profile) | no points between tanks | m | if below the minimum, add that point to section D
F. Step by step in words (updates with the numbers)
1. Flow: 21,505 m³/d in 22 h → Q = 271.5 l/s, V = 0.96 m/s in ABSTRACTION.
2. Friction (Hazen-Williams): ABSTRACTION loses hL = 0.18 m over 100 m (1.78 m/km).
3. Point 1 = MOMBA_RIVER water surface at its MINIMUM level z1 = 1361.00 m (p = 0, V ≈ 0).
4. Point 2: the hardest place to reach is MOMBA_INTAKE; it needs the HGL at the zone start to be H_req = 1360.18 m (its level + residual + losses on the way).
5. Bernoulli without pump: z1 = H_req + surplus → surplus = 1361.00 − 1360.18 = 0.82 m.
6. With the supplying tank full (MAXIMUM level 1364.50 m) the surplus is 4.32 m. A flow control valve burns this so the flow stays at design.
8. Pressure: lowest pressure along the route = no points between tanks m (minimum allowed 2 m); pipe class from section D and sheet Profile.
Note on F12: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on G12: Abstraction pipe STEEL DN600-PN10, L = 100 m ¦ ER length 100 m ¦ model length measured along the surveyed slope

## Z2 Intake-Grit
Zone 2 – Intake low-lift pumps to grit tank (pumped)
Low-lift pumps lift raw water from the intake sump into the grit tank. Pump head = level the water must reach in the grit tank + losses − sump level.
A. Inputs (levels come from sheet 'Levels')
Start: MOMBA_INTAKE MINIMUM water level | 1360 | m a.s.l. | point 1 of Bernoulli, design case (least energy at the start)
Start: MOMBA_INTAKE MAXIMUM water level | 1364 | m a.s.l. | low-head case for pumps / highest energy for gravity
Operating hours per day | 22 | h/d | ER: pumps 22 h/d; gravity 24 h/d
Static level for pressure class | 1368 | m a.s.l. | highest arrival level at the end of the zone (pipe full, pumps stopped)
Number of duty pumps | 1 | no. | working pumps sharing the flow
Number of standby pumps | 1 | no. | for information
Pump efficiency η_p | 0.75 | – | ASSUMED – use the pump curve
Motor efficiency η_m | 0.94 | – | ASSUMED
ER duty flow per pump | 978 | m³/h | Employer's Requirements
ER duty head | 10 | m | Employer's Requirements
B. Pipes – flow (continuity) and friction (Hazen-Williams)
Pipe | From | To | Upstream pipe | DN | Internal D (mm) | Length L (m) | C (H-W) | Daily volume (m³/d) | Q (m³/s) | Q (l/s) | Area (m²) | V (m/s) | hf friction (m) | hm minor (m) | hL total (m) | Gradient (m/km) | Loss before this pipe (m) | HGL start (m) | HGL end (m) | Surge Δh = aV/g (m)
LL_DELIVERY | MOMBA_INTAKE | GRIT_TANK | – | 600 | 600 | 30 | 120 | 21505.3763 | 0.27153 | 271.5325 | 0.28274 | 0.96035 | 0.048593 | 0.0048593 | 0.053452 | 1.7817 | 0 | 1369.0535 | 1369 | 97.895
C. Destinations – Bernoulli to each receiving water surface (levels from 'Levels')
Destination | Ends with pipe | MIN level (m) | MAX level (m) | Arrival level (m) | Residual (m) | z2 = arrival + residual (m) | Head needed at zone start = z2 + losses (m) | Arriving HGL, design case (m) | Excess head, design case (m) | Excess head, start at MAX level (m) | Comment
GRIT_TANK | LL_DELIVERY | 1366.5 | 1368 | 1368 | 1 | 1369 | 1369.0535 | 1369 | 0 | 4 | OK
D. Critical points along the pipes – pressure check (add your own rows)
Pipe | Chainage in pipe x (m) | Ground level (m) | Pipe crown (m) | Head needed at zone start (m) | HGL at point (m) | Pressure (m) | Static (m) | Working (m) | Working (bar) | PN required | Transient min = p − Δh (m) | Note | Status
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
E. Bernoulli result
Head needed at zone start H_req | 1369.0535 | m a.s.l. | largest of sections C, C2 (junctions) and D (points)
Set by | GRIT_TANK |  | governing destination, junction or point
Hp = H_req − z1 (suction at MINIMUM level) | 9.0535 | m | z1 + 0 + 0 + Hp = H_req (p = 0, V ≈ 0 at the sump surface)
TDH design (suction at MINIMUM level) | 12.0535 | m | Hp + station losses → size pump and motor with this
TDH low-head (suction at MAXIMUM level) | 8.0535 | m | pump must also operate here (more flow unless throttled / VFD)
Total pumped flow | 0.27153 | m³/s | flow in the first pipe
Flow per pump | 0.27153 | m³/s
Flow per pump | 977.5171 | m³/h | compare ER duty flow
Hydraulic power per pump P_h = ρgQH | 32.1072 | kW
Shaft power per pump P_s = P_h / η_p | 42.8096 | kW
Motor needed = P_s × margin | 49.231 | kW
Standard motor per pump | 55 | kW | next size up
Electricity per day | 1001.9265 | kWh/d
Specific energy | 0.04659 | kWh/m³
Electricity cost per year | 0 | per year | uses Global tariff
TDH design minus ER duty head | 2.0535 | m | negative = ER pump has spare head (throttle / VFD)
Lowest pressure at any survey point (sheet Profile) | no points between tanks | m | if below the minimum, add that point to section D
F. Step by step in words (updates with the numbers)
1. Flow: 21,505 m³/d in 22 h → Q = 271.5 l/s, V = 0.96 m/s in LL_DELIVERY.
2. Friction (Hazen-Williams): LL_DELIVERY loses hL = 0.05 m over 30 m (1.78 m/km).
3. Point 1 = MOMBA_INTAKE water surface at its MINIMUM level z1 = 1360.00 m (p = 0, V ≈ 0).
4. Point 2: the hardest place to reach is GRIT_TANK; it needs the HGL at the zone start to be H_req = 1369.05 m (its level + residual + losses on the way).
5. Bernoulli: z1 + Hp = H_req → Hp = 1369.05 − 1360.00 = 9.05 m; + station losses 3.0 m → TDH = 12.1 m.
6. With the suction tank full (MAXIMUM level 1364.00 m) TDH falls to 8.1 m: the pump must work between 8.1 and 12.1 m at 978 m³/h per pump.
7. Power: P = ρgQH/η = 43 kW per pump → motor 55 kW; ER duty head 10 m (difference +2.1 m).
8. Pressure: lowest pressure along the route = no points between tanks m (minimum allowed 2 m); pipe class from section D and sheet Profile.
Note on F18: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on G18: ASSUMED short delivery pipe low-lift PS -> grit tank ¦ model length measured along the surveyed slope

## Z3 Grit-WTP
Zone 3 – Grit tank high-lift pumps to the WTP (pumped)
High-lift pumps push raw water from the grit tank through the raw-water main into the WTP inlet (cascade aerator).
A. Inputs (levels come from sheet 'Levels')
Start: GRIT_TANK MINIMUM water level | 1366.5 | m a.s.l. | point 1 of Bernoulli, design case (least energy at the start)
Start: GRIT_TANK MAXIMUM water level | 1368 | m a.s.l. | low-head case for pumps / highest energy for gravity
Operating hours per day | 22 | h/d | ER: pumps 22 h/d; gravity 24 h/d
Static level for pressure class | 1378 | m a.s.l. | highest arrival level at the end of the zone (pipe full, pumps stopped)
Number of duty pumps | 1 | no. | working pumps sharing the flow
Number of standby pumps | 1 | no. | for information
Pump efficiency η_p | 0.75 | – | ASSUMED – use the pump curve
Motor efficiency η_m | 0.94 | – | ASSUMED
ER duty flow per pump | 978 | m³/h | Employer's Requirements
ER duty head | 25 | m | Employer's Requirements
B. Pipes – flow (continuity) and friction (Hazen-Williams)
Pipe | From | To | Upstream pipe | DN | Internal D (mm) | Length L (m) | C (H-W) | Daily volume (m³/d) | Q (m³/s) | Q (l/s) | Area (m²) | V (m/s) | hf friction (m) | hm minor (m) | hL total (m) | Gradient (m/km) | Loss before this pipe (m) | HGL start (m) | HGL end (m) | Surge Δh = aV/g (m)
RAW_MAIN | GRIT_TANK | MOMBA_WTP | – | 600 | 600 | 1078.5 | 120 | 21505.3763 | 0.27153 | 271.5325 | 0.28274 | 0.96035 | 1.7469 | 0.17469 | 1.9216 | 1.7817 | 0 | 1380.9216 | 1379 | 97.895
C. Destinations – Bernoulli to each receiving water surface (levels from 'Levels')
Destination | Ends with pipe | MIN level (m) | MAX level (m) | Arrival level (m) | Residual (m) | z2 = arrival + residual (m) | Head needed at zone start = z2 + losses (m) | Arriving HGL, design case (m) | Excess head, design case (m) | Excess head, start at MAX level (m) | Comment
MOMBA_WTP | RAW_MAIN | 1368.5 | 1373 | 1378 | 1 | 1379 | 1380.9216 | 1379 | 0 | 1.5 | OK
D. Critical points along the pipes – pressure check (add your own rows)
Pipe | Chainage in pipe x (m) | Ground level (m) | Pipe crown (m) | Head needed at zone start (m) | HGL at point (m) | Pressure (m) | Static (m) | Working (m) | Working (bar) | PN required | Transient min = p − Δh (m) | Note | Status
RAW_MAIN | 778.5 | 1372.43 | 1371.23 | 1374.6171 | 1379.5345 | 8.3045 | 6.77 | 8.3045 | 0.81467 | PN10 | -89.5905 | critical high point | OK
RAW_MAIN | 129.8 | 1365.87 | 1364.67 | 1366.9013 | 1380.6903 | 16.0203 | 13.33 | 16.0203 | 1.5716 | PN10 | -81.8747 | lowest point (highest static pressure) | OK
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
E. Bernoulli result
Head needed at zone start H_req | 1380.9216 | m a.s.l. | largest of sections C, C2 (junctions) and D (points)
Set by | MOMBA_WTP |  | governing destination, junction or point
Hp = H_req − z1 (suction at MINIMUM level) | 14.4216 | m | z1 + 0 + 0 + Hp = H_req (p = 0, V ≈ 0 at the sump surface)
TDH design (suction at MINIMUM level) | 17.4216 | m | Hp + station losses → size pump and motor with this
TDH low-head (suction at MAXIMUM level) | 15.9216 | m | pump must also operate here (more flow unless throttled / VFD)
Total pumped flow | 0.27153 | m³/s | flow in the first pipe
Flow per pump | 0.27153 | m³/s
Flow per pump | 977.5171 | m³/h | compare ER duty flow
Hydraulic power per pump P_h = ρgQH | 46.4065 | kW
Shaft power per pump P_s = P_h / η_p | 61.8754 | kW
Motor needed = P_s × margin | 71.1567 | kW
Standard motor per pump | 75 | kW | next size up
Electricity per day | 1448.1467 | kWh/d
Specific energy | 0.067339 | kWh/m³
Electricity cost per year | 0 | per year | uses Global tariff
TDH design minus ER duty head | -7.5784 | m | negative = ER pump has spare head (throttle / VFD)
Lowest pressure at any survey point (sheet Profile) | 8.3046 | m | if below the minimum, add that point to section D
F. Step by step in words (updates with the numbers)
1. Flow: 21,505 m³/d in 22 h → Q = 271.5 l/s, V = 0.96 m/s in RAW_MAIN.
2. Friction (Hazen-Williams): RAW_MAIN loses hL = 1.92 m over 1,079 m (1.78 m/km).
3. Point 1 = GRIT_TANK water surface at its MINIMUM level z1 = 1366.50 m (p = 0, V ≈ 0).
4. Point 2: the hardest place to reach is MOMBA_WTP; it needs the HGL at the zone start to be H_req = 1380.92 m (its level + residual + losses on the way).
5. Bernoulli: z1 + Hp = H_req → Hp = 1380.92 − 1366.50 = 14.42 m; + station losses 3.0 m → TDH = 17.4 m.
6. With the suction tank full (MAXIMUM level 1368.00 m) TDH falls to 15.9 m: the pump must work between 15.9 and 17.4 m at 978 m³/h per pump.
7. Power: P = ρgQH/η = 62 kW per pump → motor 75 kW; ER duty head 25 m (difference -7.6 m).
8. Pressure: lowest pressure along the route = 8.3 m (minimum allowed 2 m); pipe class from section D and sheet Profile.
Note on F18: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on G18: Raw water pipe STEEL DN600-PN10, L = 1,177 m, V = 0.97 m/s ¦ ER length 1,177 m ¦ model length measured along the surveyed slope

## Z4 WTP-Ikana
Zone 4 – WTP clear-water pumps to Ikana GBR (pumped)
The WTP pumps lift treated water about 300 m over ~20 km from the clear-water tank to Ikana GBR on the hill. Most of the head is lift; friction is the rest. Pressure is highest at the pumps.
A. Inputs (levels come from sheet 'Levels')
Start: MOMBA_WTP MINIMUM water level | 1368.5 | m a.s.l. | point 1 of Bernoulli, design case (least energy at the start)
Start: MOMBA_WTP MAXIMUM water level | 1373 | m a.s.l. | low-head case for pumps / highest energy for gravity
Operating hours per day | 22 | h/d | ER: pumps 22 h/d; gravity 24 h/d
Static level for pressure class | 1668 | m a.s.l. | highest arrival level at the end of the zone (pipe full, pumps stopped)
Number of duty pumps | 3 | no. | working pumps sharing the flow
Number of standby pumps | 1 | no. | for information
Pump efficiency η_p | 0.78 | – | ASSUMED – use the pump curve
Motor efficiency η_m | 0.95 | – | ASSUMED
ER duty flow per pump | 304 | m³/h | Employer's Requirements
ER duty head | 330 | m | Employer's Requirements
B. Pipes – flow (continuity) and friction (Hazen-Williams)
Pipe | From | To | Upstream pipe | DN | Internal D (mm) | Length L (m) | C (H-W) | Daily volume (m³/d) | Q (m³/s) | Q (l/s) | Area (m²) | V (m/s) | hf friction (m) | hm minor (m) | hL total (m) | Gradient (m/km) | Loss before this pipe (m) | HGL start (m) | HGL end (m) | Surge Δh = aV/g (m)
WTP_IKANA_RM | MOMBA_WTP | IKANA_GBR | – | 600 | 600 | 19665.6 | 120 | 20000 | 0.25253 | 252.5253 | 0.28274 | 0.89313 | 27.8477 | 2.7848 | 30.6324 | 1.5577 | 0 | 1699.6324 | 1669 | 91.0423
C. Destinations – Bernoulli to each receiving water surface (levels from 'Levels')
Destination | Ends with pipe | MIN level (m) | MAX level (m) | Arrival level (m) | Residual (m) | z2 = arrival + residual (m) | Head needed at zone start = z2 + losses (m) | Arriving HGL, design case (m) | Excess head, design case (m) | Excess head, start at MAX level (m) | Comment
IKANA_GBR | WTP_IKANA_RM | 1663.3 | 1668 | 1668 | 1 | 1669 | 1699.6324 | 1669 | 0 | 4.5 | OK
D. Critical points along the pipes – pressure check (add your own rows)
Pipe | Chainage in pipe x (m) | Ground level (m) | Pipe crown (m) | Head needed at zone start (m) | HGL at point (m) | Pressure (m) | Static (m) | Working (m) | Working (bar) | PN required | Transient min = p − Δh (m) | Note | Status
WTP_IKANA_RM | 19645.6 | 1661.36 | 1660.16 | 1692.7613 | 1669.0312 | 8.8712 | 7.84 | 8.8712 | 0.87026 | PN10 | -82.1712 | critical high point | OK
WTP_IKANA_RM | 50 | 1373.21 | 1372.01 | 1374.0879 | 1699.5545 | 327.5445 | 295.99 | 327.5445 | 32.1321 | PN40 | 236.5022 | lowest point (highest static pressure) | OK
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
E. Bernoulli result
Head needed at zone start H_req | 1699.6324 | m a.s.l. | largest of sections C, C2 (junctions) and D (points)
Set by | IKANA_GBR |  | governing destination, junction or point
Hp = H_req − z1 (suction at MINIMUM level) | 331.1324 | m | z1 + 0 + 0 + Hp = H_req (p = 0, V ≈ 0 at the sump surface)
TDH design (suction at MINIMUM level) | 334.1324 | m | Hp + station losses → size pump and motor with this
TDH low-head (suction at MAXIMUM level) | 329.6324 | m | pump must also operate here (more flow unless throttled / VFD)
Total pumped flow | 0.25253 | m³/s | flow in the first pipe
Flow per pump | 0.084175 | m³/s
Flow per pump | 303.0303 | m³/h | compare ER duty flow
Hydraulic power per pump P_h = ρgQH | 275.9124 | kW
Shaft power per pump P_s = P_h / η_p | 353.7338 | kW
Motor needed = P_s × margin | 406.7939 | kW
Standard motor per pump | 450 | kW | next size up
Electricity per day | 24575.1915 | kWh/d
Specific energy | 1.2288 | kWh/m³
Electricity cost per year | 0 | per year | uses Global tariff
TDH design minus ER duty head | 4.1324 | m | negative = ER pump has spare head (throttle / VFD)
Lowest pressure at any survey point (sheet Profile) | 8.8711 | m | if below the minimum, add that point to section D
F. Step by step in words (updates with the numbers)
1. Flow: 20,000 m³/d in 22 h → Q = 252.5 l/s, V = 0.89 m/s in WTP_IKANA_RM.
2. Friction (Hazen-Williams): WTP_IKANA_RM loses hL = 30.63 m over 19,666 m (1.56 m/km).
3. Point 1 = MOMBA_WTP water surface at its MINIMUM level z1 = 1368.50 m (p = 0, V ≈ 0).
4. Point 2: the hardest place to reach is IKANA_GBR; it needs the HGL at the zone start to be H_req = 1699.63 m (its level + residual + losses on the way).
5. Bernoulli: z1 + Hp = H_req → Hp = 1699.63 − 1368.50 = 331.13 m; + station losses 3.0 m → TDH = 334.1 m.
6. With the suction tank full (MAXIMUM level 1373.00 m) TDH falls to 329.6 m: the pump must work between 329.6 and 334.1 m at 303 m³/h per pump.
7. Power: P = ρgQH/η = 354 kW per pump → motor 450 kW; ER duty head 330 m (difference +4.1 m).
8. Pressure: lowest pressure along the route = 8.9 m (minimum allowed 2 m); pipe class from section D and sheet Profile.
Note on F18: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on G18: Rising main STEEL DN600 PN10/16/25/30/40, L = 20,994 m, V = 0.9 m/s ¦ ER length 20,994 m ¦ model length measured along the surveyed slope

## Z5 Ikana-Nkangamo
Zone 5 – Ikana GBR to Nkangamo BPS (gravity)
Water runs downhill by gravity from Ikana GBR to the Nkangamo sump. With Ikana at its MINIMUM level it must still arrive (surplus ≥ 0); any surplus is burnt by the flow control valve at the sump inlet. Static pressure uses Ikana at its MAXIMUM level.
A. Inputs (levels come from sheet 'Levels')
Start: IKANA_GBR MINIMUM water level | 1663.3 | m a.s.l. | point 1 of Bernoulli, design case (least energy at the start)
Start: IKANA_GBR MAXIMUM water level | 1668 | m a.s.l. | low-head case for pumps / highest energy for gravity
Operating hours per day | 24 | h/d | ER: pumps 22 h/d; gravity 24 h/d
Static level for pressure class | 1668 | m a.s.l. | MAXIMUM level of the supplying tank (water at rest)
B. Pipes – flow (continuity) and friction (Hazen-Williams)
Pipe | From | To | Upstream pipe | DN | Internal D (mm) | Length L (m) | C (H-W) | Daily volume (m³/d) | Q (m³/s) | Q (l/s) | Area (m²) | V (m/s) | hf friction (m) | hm minor (m) | hL total (m) | Gradient (m/km) | Loss before this pipe (m) | HGL start (m) | HGL end (m) | Surge Δh = aV/g (m)
IKANA_NKANGAMO_GM | IKANA_GBR | NKANGAMO_BPS | – | 600 | 600 | 38930.2 | 120 | 20000 | 0.23148 | 231.4815 | 0.28274 | 0.8187 | 46.9228 | 4.6923 | 51.615 | 1.3258 | 0 | 1663.3 | 1611.685 | 83.4555
C. Destinations – Bernoulli to each receiving water surface (levels from 'Levels')
Destination | Ends with pipe | MIN level (m) | MAX level (m) | Arrival level (m) | Residual (m) | z2 = arrival + residual (m) | Head needed at zone start = z2 + losses (m) | Arriving HGL, design case (m) | Excess head, design case (m) | Excess head, start at MAX level (m) | Comment
NKANGAMO_BPS | IKANA_NKANGAMO_GM | 1553 | 1557 | 1557.5 | 1 | 1558.5 | 1610.115 | 1611.685 | 53.185 | 57.885 | fit flow control valve / PRV (burns 53.2–57.9 m)
D. Critical points along the pipes – pressure check (add your own rows)
Pipe | Chainage in pipe x (m) | Ground level (m) | Pipe crown (m) | Head needed at zone start (m) | HGL at point (m) | Pressure (m) | Static (m) | Working (m) | Working (bar) | PN required | Transient min = p − Δh (m) | Note | Status
IKANA_NKANGAMO_GM | 38668.7 | 1547.62 | 1546.42 | 1599.6883 | 1612.0317 | 65.6117 | 121.58 | 121.58 | 11.927 | PN16 | -17.8438 | critical high point | OK
IKANA_NKANGAMO_GM | 31064.3 | 1450.82 | 1449.62 | 1492.8062 | 1622.1138 | 172.4938 | 218.38 | 218.38 | 21.4231 | PN25 | 89.0384 | lowest point (highest static pressure) | OK
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
E. Bernoulli result
Head needed at zone start H_req | 1610.115 | m a.s.l. | largest of sections C, C2 (junctions) and D (points)
Set by | NKANGAMO_BPS |  | governing destination, junction or point
Surplus = z1 − H_req (start at MINIMUM level) | 53.185 | m | design case: must be ≥ 0
Surplus with start at MAXIMUM level | 57.885 | m | largest head the valve must burn
Status | OK – valve burns 53.2 to 57.9 m
Lowest pressure at any survey point (sheet Profile) | 65.6117 | m | if below the minimum, add that point to section D
F. Step by step in words (updates with the numbers)
1. Flow: 20,000 m³/d in 24 h → Q = 231.5 l/s, V = 0.82 m/s in IKANA_NKANGAMO_GM.
2. Friction (Hazen-Williams): IKANA_NKANGAMO_GM loses hL = 51.62 m over 38,930 m (1.33 m/km).
3. Point 1 = IKANA_GBR water surface at its MINIMUM level z1 = 1663.30 m (p = 0, V ≈ 0).
4. Point 2: the hardest place to reach is NKANGAMO_BPS; it needs the HGL at the zone start to be H_req = 1610.12 m (its level + residual + losses on the way).
5. Bernoulli without pump: z1 = H_req + surplus → surplus = 1663.30 − 1610.12 = 53.18 m.
6. With the supplying tank full (MAXIMUM level 1668.00 m) the surplus is 57.88 m. A flow control valve burns this so the flow stays at design.
8. Pressure: lowest pressure along the route = 65.6 m (minimum allowed 2 m); pipe class from section D and sheet Profile.
Note on F12: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on G12: Gravity main STEEL DN600 PN10/16/25, L = 38,504 m, V = 0.82 m/s ¦ ER length 38,504 m ¦ model length measured along the surveyed slope

## Z6 Nkangamo-Uhuru
Zone 6 – Nkangamo BPS to Uhuru Park GBR and existing tanks (pumped)
One pump station feeds four tanks (ESR, GSR01, Ipito, Uhuru Park) and crosses a high point near 74 km. Bernoulli is applied to each; the one needing the most head sets the pumps, the others get flow control valves.
A. Inputs (levels come from sheet 'Levels')
Start: NKANGAMO_BPS MINIMUM water level | 1553 | m a.s.l. | point 1 of Bernoulli, design case (least energy at the start)
Start: NKANGAMO_BPS MAXIMUM water level | 1557 | m a.s.l. | low-head case for pumps / highest energy for gravity
Operating hours per day | 22 | h/d | ER: pumps 22 h/d; gravity 24 h/d
Static level for pressure class | 1706.5 | m a.s.l. | highest arrival level at the end of the zone (pipe full, pumps stopped)
Number of duty pumps | 2 | no. | working pumps sharing the flow
Number of standby pumps | 1 | no. | for information
Pump efficiency η_p | 0.78 | – | ASSUMED – use the pump curve
Motor efficiency η_m | 0.95 | – | ASSUMED
ER duty flow per pump | 455 | m³/h | Employer's Requirements
ER duty head | 221 | m | Employer's Requirements
B. Pipes – flow (continuity) and friction (Hazen-Williams)
Pipe | From | To | Upstream pipe | DN | Internal D (mm) | Length L (m) | C (H-W) | Daily volume (m³/d) | Q (m³/s) | Q (l/s) | Area (m²) | V (m/s) | hf friction (m) | hm minor (m) | hL total (m) | Gradient (m/km) | Loss before this pipe (m) | HGL start (m) | HGL end (m) | Surge Δh = aV/g (m)
BPS_RM_1 | NKANGAMO_BPS | J-001N | – | 600 | 600 | 19581.4 | 120 | 20000 | 0.25253 | 252.5253 | 0.28274 | 0.89313 | 27.7284 | 2.7728 | 30.5013 | 1.5577 | 0 | 1738.2284 | 1707.7271 | 91.0423
BPS_RM_2 | J-001N | J-002N | BPS_RM_1 | 600 | 600 | 40 | 120 | 19628.48 | 0.24783 | 247.8343 | 0.28274 | 0.87653 | 0.054709 | 0.0054709 | 0.06018 | 1.5045 | 30.5013 | 1707.7271 | 1707.6669 | 89.3511
BPS_RM_3 | J-002N | J-003N | BPS_RM_2 | 600 | 600 | 100.2 | 120 | 18081.92 | 0.22831 | 228.3071 | 0.28274 | 0.80747 | 0.11772 | 0.011772 | 0.12949 | 1.2924 | 30.5614 | 1707.6669 | 1707.5375 | 82.311
UHURU_INLET | J-003N | UHURU_PARK_GBR | BPS_RM_3 | 600 | 600 | 50 | 120 | 17459.82 | 0.22045 | 220.4523 | 0.28274 | 0.77969 | 0.055056 | 0.0055056 | 0.060561 | 1.2112 | 30.6909 | 1707.5375 | 1707.4769 | 79.4791
ESR_BRANCH | J-001N | TUNDUMA_ESR | BPS_RM_1 | 100 | 100 | 38 | 120 | 371.52 | 0.0046909 | 4.6909 | 0.007854 | 0.59727 | 0.20648 | 0.020648 | 0.22713 | 5.977 | 30.5013 | 1707.7271 | 1707.5 | 60.8833
GSR01_BRANCH | J-002N | UHURU_GSR01 | BPS_RM_2 | 150 | 150 | 40 | 120 | 1546.56 | 0.019527 | 19.5273 | 0.017671 | 1.105 | 0.42327 | 0.042327 | 0.46559 | 11.6398 | 30.5614 | 1707.6669 | 1707.2014 | 112.642
IPITO_BRANCH | J-003N | IPITO_GSR02 | BPS_RM_3 | 150 | 150 | 4220.8 | 120 | 622.1 | 0.0078548 | 7.8548 | 0.017671 | 0.44449 | 8.2693 | 0.82693 | 9.0963 | 2.1551 | 30.6909 | 1707.5375 | 1698.4412 | 45.31
C. Destinations – Bernoulli to each receiving water surface (levels from 'Levels')
Destination | Ends with pipe | MIN level (m) | MAX level (m) | Arrival level (m) | Residual (m) | z2 = arrival + residual (m) | Head needed at zone start = z2 + losses (m) | Arriving HGL, design case (m) | Excess head, design case (m) | Excess head, start at MAX level (m) | Comment
TUNDUMA_ESR | ESR_BRANCH | 1703.5 | 1706.5 | 1706.5 | 1 | 1707.5 | 1738.2284 | 1707.5 | 0 | 4 | OK
UHURU_GSR01 | GSR01_BRANCH | 1698.4 | 1701.4 | 1701.4 | 1 | 1702.4 | 1733.427 | 1707.2014 | 4.8014 | 8.8014 | fit flow control valve / PRV (burns 4.8–8.8 m)
IPITO_GSR02 | IPITO_BRANCH | 1681.2 | 1684.2 | 1684.2 | 1 | 1685.2 | 1724.9872 | 1698.4412 | 13.2412 | 17.2412 | fit flow control valve / PRV (burns 13.2–17.2 m)
UHURU_PARK_GBR | UHURU_INLET | 1697.6 | 1702.3 | 1702.3 | 1 | 1703.3 | 1734.0515 | 1707.4769 | 4.1769 | 8.1769 | fit flow control valve / PRV (burns 4.2–8.2 m)
C2. Junctions – minimum pressure at offtakes (ER Table 7)
Junction | End of pipe | Ground level (m) | Minimum pressure (m) | Head needed at zone start = ground + p_min + losses (m) | HGL at junction (m) | Pressure (m) | Status
J-001N | BPS_RM_1 | 1698.34 | 5 | 1733.8413 | 1707.7271 | 9.3871 | OK
J-002N | BPS_RM_2 | 1699.25 | 5 | 1734.8114 | 1707.6669 | 8.4169 | OK
J-003N | BPS_RM_3 | 1699.34 | 5 | 1735.0309 | 1707.5375 | 8.1975 | OK
D. Critical points along the pipes – pressure check (add your own rows)
Pipe | Chainage in pipe x (m) | Ground level (m) | Pipe crown (m) | Head needed at zone start (m) | HGL at point (m) | Pressure (m) | Static (m) | Working (m) | Working (bar) | PN required | Transient min = p − Δh (m) | Note | Status
BPS_RM_1 | 14583.1 | 1710.04 | 1708.84 | 1733.5556 | 1715.5128 | 6.6728 | -2.34 | 6.6728 | 0.6546 | PN10 | -84.3695 | critical high point | OK
BPS_RM_1 | 5635.7 | 1561.57 | 1560.37 | 1571.1485 | 1729.4499 | 169.0799 | 146.13 | 169.0799 | 16.5867 | PN25 | 78.0375 | lowest point (highest static pressure) | OK
IPITO_BRANCH | 145 | 1699.45 | 1698.25 | 1731.2534 | 1707.225 | 8.975 | 8.25 | 8.975 | 0.88044 | PN10 | -36.335 | critical high point | OK
IPITO_BRANCH | 3317.8 | 1603.64 | 1602.44 | 1642.2811 | 1700.3872 | 97.9472 | 104.06 | 104.06 | 10.2083 | PN16 | 52.6373 | lowest point (highest static pressure) | OK
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
E. Bernoulli result
Head needed at zone start H_req | 1738.2284 | m a.s.l. | largest of sections C, C2 (junctions) and D (points)
Set by | TUNDUMA_ESR |  | governing destination, junction or point
Hp = H_req − z1 (suction at MINIMUM level) | 185.2284 | m | z1 + 0 + 0 + Hp = H_req (p = 0, V ≈ 0 at the sump surface)
TDH design (suction at MINIMUM level) | 188.2284 | m | Hp + station losses → size pump and motor with this
TDH low-head (suction at MAXIMUM level) | 184.2284 | m | pump must also operate here (more flow unless throttled / VFD)
Total pumped flow | 0.25253 | m³/s | flow in the first pipe
Flow per pump | 0.12626 | m³/s
Flow per pump | 454.5455 | m³/h | compare ER duty flow
Hydraulic power per pump P_h = ρgQH | 233.1465 | kW
Shaft power per pump P_s = P_h / η_p | 298.9058 | kW
Motor needed = P_s × margin | 343.7417 | kW
Standard motor per pump | 355 | kW | next size up
Electricity per day | 13844.0583 | kWh/d
Specific energy | 0.6922 | kWh/m³
Electricity cost per year | 0 | per year | uses Global tariff
TDH design minus ER duty head | -32.7716 | m | negative = ER pump has spare head (throttle / VFD)
Lowest pressure at any survey point (sheet Profile) | 6.6727 | m | if below the minimum, add that point to section D
F. Step by step in words (updates with the numbers)
1. Flow: 20,000 m³/d in 22 h → Q = 252.5 l/s, V = 0.89 m/s in BPS_RM_1.
2. Friction (Hazen-Williams): BPS_RM_1 loses hL = 30.50 m over 19,581 m (1.56 m/km).
3. Point 1 = NKANGAMO_BPS water surface at its MINIMUM level z1 = 1553.00 m (p = 0, V ≈ 0).
4. Point 2: the hardest place to reach is TUNDUMA_ESR; it needs the HGL at the zone start to be H_req = 1738.23 m (its level + residual + losses on the way).
5. Bernoulli: z1 + Hp = H_req → Hp = 1738.23 − 1553.00 = 185.23 m; + station losses 3.0 m → TDH = 188.2 m.
6. With the suction tank full (MAXIMUM level 1557.00 m) TDH falls to 184.2 m: the pump must work between 184.2 and 188.2 m at 455 m³/h per pump.
7. Power: P = ρgQH/η = 299 kW per pump → motor 355 kW; ER duty head 221 m (difference -32.8 m).
8. Pressure: lowest pressure along the route = 6.7 m (minimum allowed 2 m); pipe class from section D and sheet Profile.
Note on F18: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on F19: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on F20: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on F21: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on F22: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on F23: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on F24: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on G18: Rising main STEEL DN600 PN10/16/25, L = 21,673 m (BPS -> Uhuru Park), V = 0.9 m/s ¦ ER length 21,673 m ¦ model length measured along the surveyed slope
Note on G19: ¦ model length measured along the surveyed slope
Note on G20: ¦ model length measured along the surveyed slope
Note on G21: ASSUMED 50 m from J-003N to the Uhuru Park GBR inlet ¦ model length measured along the surveyed slope
Note on G22: STEEL DN100-PN10, L = 38 m (schematic label DN80) ¦ ER length 38 m ¦ model length measured along the surveyed slope
Note on G23: STEEL DN150-PN16, L = 40 m ¦ ER length 40 m ¦ model length measured along the surveyed slope
Note on G24: STEEL DN150-PN10, L = 4,285 m ¦ ER length 4,285 m ¦ model length measured along the surveyed slope

## Z7 Uhuru-Chapwa
Zone 7 – Uhuru Park GBR to Makambini and Chapwa (gravity)
Uhuru Park GBR feeds Makambini and Chapwa by gravity through J-004N. Chapwa is far below, so it arrives with large excess head (valve + higher PN). Check the points near the GBR: the ground there is close to the tank level.
A. Inputs (levels come from sheet 'Levels')
Start: UHURU_PARK_GBR MINIMUM water level | 1697.6 | m a.s.l. | point 1 of Bernoulli, design case (least energy at the start)
Start: UHURU_PARK_GBR MAXIMUM water level | 1702.3 | m a.s.l. | low-head case for pumps / highest energy for gravity
Operating hours per day | 24 | h/d | ER: pumps 22 h/d; gravity 24 h/d
Static level for pressure class | 1702.3 | m a.s.l. | MAXIMUM level of the supplying tank (water at rest)
B. Pipes – flow (continuity) and friction (Hazen-Williams)
Pipe | From | To | Upstream pipe | DN | Internal D (mm) | Length L (m) | C (H-W) | Daily volume (m³/d) | Q (m³/s) | Q (l/s) | Area (m²) | V (m/s) | hf friction (m) | hm minor (m) | hL total (m) | Gradient (m/km) | Loss before this pipe (m) | HGL start (m) | HGL end (m) | Surge Δh = aV/g (m)
UHURU_J004N | UHURU_PARK_GBR | J-004N | – | 150 | 150 | 1563.5 | 120 | 1244.2 | 0.0144 | 14.4005 | 0.017671 | 0.8149 | 9.4123 | 0.94123 | 10.3536 | 6.622 | 0 | 1697.6 | 1687.2464 | 83.0682
MAKAMBINI_BRANCH | J-004N | MAKAMBINI_GSR03 | UHURU_J004N | 100 | 100 | 494 | 120 | 622.1 | 0.0072002 | 7.2002 | 0.007854 | 0.91676 | 5.9354 | 0.59354 | 6.529 | 13.2166 | 10.3536 | 1687.2464 | 1680.7175 | 93.4518
CHAPWA_BRANCH | J-004N | CHAPWA_GSR04 | UHURU_J004N | 100 | 100 | 2790.5 | 120 | 622.1 | 0.0072002 | 7.2002 | 0.007854 | 0.91676 | 33.5281 | 3.3528 | 36.8809 | 13.2166 | 10.3536 | 1687.2464 | 1650.3656 | 93.4518
C. Destinations – Bernoulli to each receiving water surface (levels from 'Levels')
Destination | Ends with pipe | MIN level (m) | MAX level (m) | Arrival level (m) | Residual (m) | z2 = arrival + residual (m) | Head needed at zone start = z2 + losses (m) | Arriving HGL, design case (m) | Excess head, design case (m) | Excess head, start at MAX level (m) | Comment
MAKAMBINI_GSR03 | MAKAMBINI_BRANCH | 1655.7 | 1658.7 | 1658.7 | 1 | 1659.7 | 1676.5825 | 1680.7175 | 21.0175 | 25.7175 | fit flow control valve / PRV (burns 21.0–25.7 m)
CHAPWA_GSR04 | CHAPWA_BRANCH | 1521.4 | 1524.4 | 1524.4 | 1 | 1525.4 | 1572.6344 | 1650.3656 | 124.9656 | 129.6656 | fit flow control valve / PRV (burns 125.0–129.7 m)
C2. Junctions – minimum pressure at offtakes (ER Table 7)
Junction | End of pipe | Ground level (m) | Minimum pressure (m) | Head needed at zone start = ground + p_min + losses (m) | HGL at junction (m) | Pressure (m) | Status
J-004N | UHURU_J004N | 1630.08 | 5 | 1645.4336 | 1687.2464 | 57.1664 | OK
D. Critical points along the pipes – pressure check (add your own rows)
Pipe | Chainage in pipe x (m) | Ground level (m) | Pipe crown (m) | Head needed at zone start (m) | HGL at point (m) | Pressure (m) | Static (m) | Working (m) | Working (bar) | PN required | Transient min = p − Δh (m) | Note | Status
UHURU_J004N | 179.3 | 1699.52 | 1698.32 | 1701.5073 | 1696.4127 | -1.9073 | 3.98 | 3.98 | 0.39044 | PN10 | -84.9756 | critical high point | NEGATIVE PRESSURE
UHURU_J004N | 1514.5 | 1633.93 | 1632.73 | 1644.7591 | 1687.5709 | 54.8409 | 69.57 | 69.57 | 6.8248 | PN10 | -28.2273 | lowest point (highest static pressure) | OK
CHAPWA_BRANCH | 0 | 1630.08 | 1628.88 | 1641.2336 | 1687.2464 | 58.3664 | 73.42 | 73.42 | 7.2025 | PN10 | -35.0853 | governing point (model) | OK
CHAPWA_BRANCH | 50 | 1628.93 | 1627.73 | 1640.7444 | 1686.5856 | 58.8556 | 74.57 | 74.57 | 7.3153 | PN10 | -34.5962 | critical high point | OK
CHAPWA_BRANCH | 2781.8 | 1523.93 | 1522.73 | 1571.8494 | 1650.4806 | 127.7506 | 179.57 | 179.57 | 17.6158 | PN25 | 34.2988 | lowest point (highest static pressure) | OK
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
add a point: pipe ID, chainage, ground level
E. Bernoulli result
Head needed at zone start H_req | 1701.5073 | m a.s.l. | largest of sections C, C2 (junctions) and D (points)
Set by | point on UHURU_J004N |  | governing destination, junction or point
Surplus = z1 − H_req (start at MINIMUM level) | -3.9073 | m | design case: must be ≥ 0
Surplus with start at MAXIMUM level | 0.79267 | m | largest head the valve must burn
Status | SHORT OF HEAD at minimum level – bigger pipe, lower outlet, higher tank or pump
Lowest pressure at any survey point (sheet Profile) | -1.9076 | m | if below the minimum, add that point to section D
F. Step by step in words (updates with the numbers)
1. Flow: 1,244 m³/d in 24 h → Q = 14.4 l/s, V = 0.81 m/s in UHURU_J004N.
2. Friction (Hazen-Williams): UHURU_J004N loses hL = 10.35 m over 1,564 m (6.62 m/km).
3. Point 1 = UHURU_PARK_GBR water surface at its MINIMUM level z1 = 1697.60 m (p = 0, V ≈ 0).
4. Point 2: the hardest place to reach is point on UHURU_J004N; it needs the HGL at the zone start to be H_req = 1701.51 m (its level + residual + losses on the way).
5. Bernoulli without pump: z1 = H_req + surplus → surplus = 1697.60 − 1701.51 = -3.91 m.
6. With the supplying tank full (MAXIMUM level 1702.30 m) the surplus is 0.79 m. Negative at minimum level: the zone cannot deliver – change pipe or levels.
8. Pressure: lowest pressure along the route = -1.9 m (minimum allowed 2 m); pipe class from section D and sheet Profile.
Note on F12: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on F13: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on F14: Internal diameter. Defaults to DN; overwrite with the real ID (e.g. lined steel) if known.
Note on G12: Gravity STEEL DN150-PN10, L = 1,555 m, Q = 1,244.2 m3/day ¦ ER length 1,555 m ¦ model length measured along the surveyed slope
Note on G13: STEEL DN100-PN10, L = 494 m (route not surveyed - straight line) ¦ ER length 494 m ¦ model length measured along the surveyed slope
Note on G14: STEEL DN100-PN25, L = 2,664 m ¦ ER length 2,664 m ¦ model length measured along the surveyed slope

## Storage
Storage – balancing for pump rest hours
V_bal = inflow × (1 − hours/24); emergency = inflow × hours/24. Volumes and levels from 'Levels'.
Tank | MIN level (m) | MAX level (m) | Daily inflow (m³/d) | Inflow hours (h/d) | Balancing volume (m³) | Emergency hours | Emergency volume (m³) | Required (m³) | Capacity (m³) | Storage (h of flow) | Status
IKANA_GBR | 1663.3 | 1668 | 20000 | 22 | 1666.6667 | 0 | 0 | 1666.6667 | 3000 | 3.6 | OK
NKANGAMO_BPS | 1553 | 1557 | 20000 | 22 | 1666.6667 | 0 | 0 | 1666.6667 | 2000 | 2.4 | OK
UHURU_PARK_GBR | 1697.6 | 1702.3 | 17459.82 | 22 | 1454.985 | 0 | 0 | 1454.985 | 5000 | 6.8729 | OK
TUNDUMA_ESR | 1703.5 | 1706.5 | 371.52 | 22 | 30.96 | 0 | 0 | 30.96 | 120 | 7.7519 | OK
UHURU_GSR01 | 1698.4 | 1701.4 | 1546.56 | 22 | 128.88 | 0 | 0 | 128.88 | 500 | 7.7592 | OK
IPITO_GSR02 | 1681.2 | 1684.2 | 622.1 | 22 | 51.8417 | 0 | 0 | 51.8417 | 200 | 7.7158 | OK
MAKAMBINI_GSR03 | 1655.7 | 1658.7 | 622.1 | 24 | 0 | 0 | 0 | 0 | 200 | 7.7158 | OK
CHAPWA_GSR04 | 1521.4 | 1524.4 | 622.1 | 24 | 0 | 0 | 0 | 0 | 200 | 7.7158 | OK
Note on E6: Sump receives 24 h gravity flow and is emptied by the BPS pumps in these hours: it must hold the inflow during the pump-off period.

## Profile
Pressure at every surveyed point
HGL from the zone sheets; ground from the topographic survey. Column L = 'no' for pipe ends at a water surface (not checked).
Zone | Pipe | Chainage in pipe (m) | Ground (m) | Pipe crown (m) | HGL (m) | Static (m) | Pressure (m) | Working (m) | PN required | Status | Check?
Z1 River-Intake | ABSTRACTION | 0 | 1360.2 | 1359 | 1361 | 5.5 | 2 | 5.5 | PN10 | end at tank | no
Z1 River-Intake | ABSTRACTION | 100 | 1360 | 1358.8 | 1360.8218 | 5.7 | 2.0218 | 5.7 | PN10 | end at tank | no
Z2 Intake-Grit | LL_DELIVERY | 0 | 1365.94 | 1364.74 | 1369.0535 | 3.26 | 4.3135 | 4.3135 | PN10 | end at tank | no
Z2 Intake-Grit | LL_DELIVERY | 30 | 1365.94 | 1364.74 | 1369 | 3.26 | 4.26 | 4.26 | PN10 | end at tank | no
Z3 Grit-WTP | RAW_MAIN | 0 | 1365.94 | 1364.74 | 1380.9216 | 13.26 | 16.1816 | 16.1816 | PN10 | end at tank | no
Z3 Grit-WTP | RAW_MAIN | 129.83 | 1365.87 | 1364.67 | 1380.6903 | 13.33 | 16.0203 | 16.0203 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 179.83 | 1366.02 | 1364.82 | 1380.6012 | 13.18 | 15.7812 | 15.7812 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 229.83 | 1366.08 | 1364.88 | 1380.5121 | 13.12 | 15.6321 | 15.6321 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 279.83 | 1366.21 | 1365.01 | 1380.423 | 12.99 | 15.413 | 15.413 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 329.83 | 1366.33 | 1365.13 | 1380.3339 | 12.87 | 15.2039 | 15.2039 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 379.84 | 1367.37 | 1366.17 | 1380.2448 | 11.83 | 14.0748 | 14.0748 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 429.85 | 1368.42 | 1367.22 | 1380.1557 | 10.78 | 12.9357 | 12.9357 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 479.88 | 1370.17 | 1368.97 | 1380.0666 | 9.03 | 11.0966 | 11.0966 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 529.89 | 1371.2 | 1370 | 1379.9775 | 8 | 9.9775 | 9.9775 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 578.45 | 1372.47 | 1371.27 | 1379.891 | 6.73 | 8.621 | 8.621 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 628.45 | 1371.99 | 1370.79 | 1379.8019 | 7.21 | 9.0119 | 9.0119 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 678.45 | 1372.35 | 1371.15 | 1379.7128 | 6.85 | 8.5628 | 8.5628 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 728.45 | 1372.37 | 1371.17 | 1379.6237 | 6.83 | 8.4537 | 8.4537 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 778.45 | 1372.43 | 1371.23 | 1379.5346 | 6.77 | 8.3046 | 8.3046 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 828.45 | 1372.18 | 1370.98 | 1379.4455 | 7.02 | 8.4655 | 8.4655 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 878.45 | 1372.1 | 1370.9 | 1379.3564 | 7.1 | 8.4564 | 8.4564 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 928.46 | 1371.84 | 1370.64 | 1379.2673 | 7.36 | 8.6273 | 8.6273 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 978.46 | 1371.59 | 1370.39 | 1379.1782 | 7.61 | 8.7882 | 8.7882 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 1028.46 | 1371.93 | 1370.73 | 1379.0892 | 7.27 | 8.3592 | 8.3592 | PN10 | OK | yes
Z3 Grit-WTP | RAW_MAIN | 1078.46 | 1372.2 | 1371 | 1379.0001 | 7 | 8.0001 | 8.0001 | PN10 | end at tank | no
Z4 WTP-Ikana | WTP_IKANA_RM | 0 | 1372.2 | 1371 | 1699.6324 | 297 | 328.6324 | 328.6324 | PN40 | end at tank | no
Z4 WTP-Ikana | WTP_IKANA_RM | 50.01 | 1373.21 | 1372.01 | 1699.5545 | 295.99 | 327.5445 | 327.5445 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 100.02 | 1374.1 | 1372.9 | 1699.4766 | 295.1 | 326.5766 | 326.5766 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 150.03 | 1375.25 | 1374.05 | 1699.3987 | 293.95 | 325.3487 | 325.3487 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 200.04 | 1376.32 | 1375.12 | 1699.3208 | 292.88 | 324.2008 | 324.2008 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 250.05 | 1377.16 | 1375.96 | 1699.2429 | 292.04 | 323.2829 | 323.2829 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 300.08 | 1378.79 | 1377.59 | 1699.165 | 290.41 | 321.575 | 321.575 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 350.09 | 1379.95 | 1378.75 | 1699.0871 | 289.25 | 320.3371 | 320.3371 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 400.12 | 1381.63 | 1380.43 | 1699.0092 | 287.57 | 318.5792 | 318.5792 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 450.15 | 1383.37 | 1382.17 | 1698.9312 | 285.83 | 316.7612 | 316.7612 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 500.16 | 1384.37 | 1383.17 | 1698.8533 | 284.83 | 315.6833 | 315.6833 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 550.19 | 1386.2 | 1385 | 1698.7754 | 283 | 313.7754 | 313.7754 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 600.21 | 1387.64 | 1386.44 | 1698.6975 | 281.56 | 312.2575 | 312.2575 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 650.22 | 1388.72 | 1387.52 | 1698.6196 | 280.48 | 311.0996 | 311.0996 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 700.24 | 1389.8 | 1388.6 | 1698.5417 | 279.4 | 309.9417 | 309.9417 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 750.24 | 1390.58 | 1389.38 | 1698.4638 | 278.62 | 309.0838 | 309.0838 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 800.24 | 1390.97 | 1389.77 | 1698.3859 | 278.23 | 308.6159 | 308.6159 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 850.24 | 1391.04 | 1389.84 | 1698.308 | 278.16 | 308.468 | 308.468 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 900.24 | 1390.7 | 1389.5 | 1698.2301 | 278.5 | 308.7301 | 308.7301 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 950.25 | 1390.44 | 1389.24 | 1698.1522 | 278.76 | 308.9122 | 308.9122 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1000.25 | 1389.94 | 1388.74 | 1698.0744 | 279.26 | 309.3344 | 309.3344 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1050.25 | 1389.31 | 1388.11 | 1697.9965 | 279.89 | 309.8865 | 309.8865 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1100.26 | 1388.49 | 1387.29 | 1697.9186 | 280.71 | 310.6286 | 310.6286 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1150.26 | 1388.22 | 1387.02 | 1697.8407 | 280.98 | 310.8207 | 310.8207 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1200.26 | 1387.99 | 1386.79 | 1697.7628 | 281.21 | 310.9728 | 310.9728 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1250.26 | 1388.63 | 1387.43 | 1697.6849 | 280.57 | 310.2549 | 310.2549 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1300.28 | 1389.69 | 1388.49 | 1697.607 | 279.51 | 309.117 | 309.117 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1350.28 | 1390.51 | 1389.31 | 1697.5291 | 278.69 | 308.2191 | 308.2191 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1400.3 | 1391.89 | 1390.69 | 1697.4512 | 277.31 | 306.7612 | 306.7612 | PN40 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1450.32 | 1393.24 | 1392.04 | 1697.3733 | 275.96 | 305.3333 | 305.3333 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1500.35 | 1394.99 | 1393.79 | 1697.2954 | 274.21 | 303.5054 | 303.5054 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1550.39 | 1396.88 | 1395.68 | 1697.2174 | 272.32 | 301.5374 | 301.5374 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1600.4 | 1398.17 | 1396.97 | 1697.1395 | 271.03 | 300.1695 | 300.1695 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1650.41 | 1398.98 | 1397.78 | 1697.0616 | 270.22 | 299.2816 | 299.2816 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1700.42 | 1399.83 | 1398.63 | 1696.9837 | 269.37 | 298.3537 | 298.3537 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1750.42 | 1400.71 | 1399.51 | 1696.9059 | 268.49 | 297.3959 | 297.3959 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1800.43 | 1401.28 | 1400.08 | 1696.828 | 267.92 | 296.748 | 296.748 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1850.44 | 1402.51 | 1401.31 | 1696.7501 | 266.69 | 295.4401 | 295.4401 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1886.63 | 1403.71 | 1402.51 | 1696.6937 | 265.49 | 294.1837 | 294.1837 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1936.63 | 1403.85 | 1402.65 | 1696.6158 | 265.35 | 293.9658 | 293.9658 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 1986.66 | 1402.19 | 1400.99 | 1696.5379 | 267.01 | 295.5479 | 295.5479 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2036.66 | 1402.74 | 1401.54 | 1696.46 | 266.46 | 294.92 | 294.92 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2086.68 | 1404.09 | 1402.89 | 1696.3821 | 265.11 | 293.4921 | 293.4921 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2136.7 | 1405.49 | 1404.29 | 1696.3042 | 263.71 | 292.0142 | 292.0142 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2186.73 | 1407.13 | 1405.93 | 1696.2262 | 262.07 | 290.2962 | 290.2962 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2236.7 | 1406.31 | 1405.11 | 1696.1484 | 262.89 | 291.0384 | 291.0384 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2339.16 | 1406.47 | 1405.27 | 1695.9888 | 262.73 | 290.7188 | 290.7188 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2389.16 | 1406 | 1404.8 | 1695.9109 | 263.2 | 291.1109 | 291.1109 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2439.25 | 1403.04 | 1401.84 | 1695.8329 | 266.16 | 293.9929 | 293.9929 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2489.25 | 1403.22 | 1402.02 | 1695.755 | 265.98 | 293.735 | 293.735 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2539.26 | 1403.75 | 1402.55 | 1695.6771 | 265.45 | 293.1271 | 293.1271 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2589.26 | 1403.8 | 1402.6 | 1695.5992 | 265.4 | 292.9992 | 292.9992 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2626.71 | 1402.97 | 1401.77 | 1695.5409 | 266.23 | 293.7709 | 293.7709 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2676.72 | 1403.86 | 1402.66 | 1695.463 | 265.34 | 292.803 | 292.803 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2726.72 | 1404.24 | 1403.04 | 1695.3851 | 264.96 | 292.3451 | 292.3451 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2776.74 | 1405.35 | 1404.15 | 1695.3072 | 263.85 | 291.1572 | 291.1572 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2826.74 | 1405.88 | 1404.68 | 1695.2293 | 263.32 | 290.5493 | 290.5493 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2876.75 | 1406.79 | 1405.59 | 1695.1514 | 262.41 | 289.5614 | 289.5614 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2926.75 | 1406.98 | 1405.78 | 1695.0735 | 262.22 | 289.2935 | 289.2935 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 2976.75 | 1407.6 | 1406.4 | 1694.9956 | 261.6 | 288.5956 | 288.5956 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3026.75 | 1407.88 | 1406.68 | 1694.9178 | 261.32 | 288.2378 | 288.2378 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3076.76 | 1408.59 | 1407.39 | 1694.8399 | 260.61 | 287.4499 | 287.4499 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3126.76 | 1409.33 | 1408.13 | 1694.762 | 259.87 | 286.632 | 286.632 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3176.77 | 1410.25 | 1409.05 | 1694.6841 | 258.95 | 285.6341 | 285.6341 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3226.78 | 1410.87 | 1409.67 | 1694.6062 | 258.33 | 284.9362 | 284.9362 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3276.78 | 1411.46 | 1410.26 | 1694.5283 | 257.74 | 284.2683 | 284.2683 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3326.79 | 1412.28 | 1411.08 | 1694.4504 | 256.92 | 283.3704 | 283.3704 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3376.79 | 1412.95 | 1411.75 | 1694.3725 | 256.25 | 282.6225 | 282.6225 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3426.79 | 1413.43 | 1412.23 | 1694.2946 | 255.77 | 282.0646 | 282.0646 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3476.8 | 1414.25 | 1413.05 | 1694.2167 | 254.95 | 281.1667 | 281.1667 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3526.8 | 1414.68 | 1413.48 | 1694.1388 | 254.52 | 280.6588 | 280.6588 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3576.14 | 1415.15 | 1413.95 | 1694.062 | 254.05 | 280.112 | 280.112 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3626.14 | 1415.51 | 1414.31 | 1693.9841 | 253.69 | 279.6741 | 279.6741 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3676.14 | 1415.48 | 1414.28 | 1693.9062 | 253.72 | 279.6262 | 279.6262 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3726.15 | 1415.18 | 1413.98 | 1693.8283 | 254.02 | 279.8483 | 279.8483 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3776.15 | 1414.66 | 1413.46 | 1693.7504 | 254.54 | 280.2904 | 280.2904 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3826.15 | 1414.13 | 1412.93 | 1693.6726 | 255.07 | 280.7426 | 280.7426 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3876.16 | 1413.3 | 1412.1 | 1693.5947 | 255.9 | 281.4947 | 281.4947 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3926.16 | 1412.71 | 1411.51 | 1693.5168 | 256.49 | 282.0068 | 282.0068 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 3976.17 | 1411.74 | 1410.54 | 1693.4389 | 257.46 | 282.8989 | 282.8989 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4026.18 | 1410.83 | 1409.63 | 1693.361 | 258.37 | 283.731 | 283.731 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4076.19 | 1409.98 | 1408.78 | 1693.2831 | 259.22 | 284.5031 | 284.5031 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4126.19 | 1409.52 | 1408.32 | 1693.2052 | 259.68 | 284.8852 | 284.8852 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4176.2 | 1408.29 | 1407.09 | 1693.1273 | 260.91 | 286.0373 | 286.0373 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4226.21 | 1407.4 | 1406.2 | 1693.0494 | 261.8 | 286.8494 | 286.8494 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4276.22 | 1406.76 | 1405.56 | 1692.9715 | 262.44 | 287.4115 | 287.4115 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4326.23 | 1405.66 | 1404.46 | 1692.8936 | 263.54 | 288.4336 | 288.4336 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4376.23 | 1405.1 | 1403.9 | 1692.8157 | 264.1 | 288.9157 | 288.9157 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4426.23 | 1404.58 | 1403.38 | 1692.7378 | 264.62 | 289.3578 | 289.3578 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4476.23 | 1404.75 | 1403.55 | 1692.66 | 264.45 | 289.11 | 289.11 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4526.23 | 1404.56 | 1403.36 | 1692.5821 | 264.64 | 289.2221 | 289.2221 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4576.23 | 1404.66 | 1403.46 | 1692.5042 | 264.54 | 289.0442 | 289.0442 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4626.23 | 1404.89 | 1403.69 | 1692.4263 | 264.31 | 288.7363 | 288.7363 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4676.23 | 1404.9 | 1403.7 | 1692.3484 | 264.3 | 288.6484 | 288.6484 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4726.23 | 1405.1 | 1403.9 | 1692.2705 | 264.1 | 288.3705 | 288.3705 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4776.24 | 1405.39 | 1404.19 | 1692.1926 | 263.81 | 288.0026 | 288.0026 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4826.25 | 1406.54 | 1405.34 | 1692.1147 | 262.66 | 286.7747 | 286.7747 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4876.25 | 1405.8 | 1404.6 | 1692.0369 | 263.4 | 287.4369 | 287.4369 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4926.25 | 1405.79 | 1404.59 | 1691.959 | 263.41 | 287.369 | 287.369 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 4976.25 | 1405.89 | 1404.69 | 1691.8811 | 263.31 | 287.1911 | 287.1911 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5026.25 | 1406.14 | 1404.94 | 1691.8032 | 263.06 | 286.8632 | 286.8632 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5076.26 | 1406.53 | 1405.33 | 1691.7253 | 262.67 | 286.3953 | 286.3953 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5126.26 | 1406.99 | 1405.79 | 1691.6474 | 262.21 | 285.8574 | 285.8574 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5176.26 | 1407.45 | 1406.25 | 1691.5695 | 261.75 | 285.3195 | 285.3195 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5226.26 | 1407.79 | 1406.59 | 1691.4917 | 261.41 | 284.9017 | 284.9017 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5276.26 | 1408.18 | 1406.98 | 1691.4138 | 261.02 | 284.4338 | 284.4338 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5326.27 | 1408.98 | 1407.78 | 1691.3359 | 260.22 | 283.5559 | 283.5559 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5376.27 | 1409.62 | 1408.42 | 1691.258 | 259.58 | 282.838 | 282.838 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5426.28 | 1410.26 | 1409.06 | 1691.1801 | 258.94 | 282.1201 | 282.1201 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5476.28 | 1410.7 | 1409.5 | 1691.1022 | 258.5 | 281.6022 | 281.6022 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5526.28 | 1411.31 | 1410.11 | 1691.0243 | 257.89 | 280.9143 | 280.9143 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5576.29 | 1411.85 | 1410.65 | 1690.9464 | 257.35 | 280.2964 | 280.2964 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5626.29 | 1412.28 | 1411.08 | 1690.8685 | 256.92 | 279.7885 | 279.7885 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5676.29 | 1413.04 | 1411.84 | 1690.7907 | 256.16 | 278.9507 | 278.9507 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5726.3 | 1413.79 | 1412.59 | 1690.7128 | 255.41 | 278.1228 | 278.1228 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5776.3 | 1414.05 | 1412.85 | 1690.6349 | 255.15 | 277.7849 | 277.7849 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5826.31 | 1415.1 | 1413.9 | 1690.557 | 254.1 | 276.657 | 276.657 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5876.31 | 1415.26 | 1414.06 | 1690.4791 | 253.94 | 276.4191 | 276.4191 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5926.32 | 1416.17 | 1414.97 | 1690.4012 | 253.03 | 275.4312 | 275.4312 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 5976.32 | 1416.66 | 1415.46 | 1690.3233 | 252.54 | 274.8633 | 274.8633 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6026.35 | 1418.37 | 1417.17 | 1690.2454 | 250.83 | 273.0754 | 273.0754 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6076.35 | 1417.86 | 1416.66 | 1690.1675 | 251.34 | 273.5075 | 273.5075 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6126.36 | 1418.47 | 1417.27 | 1690.0896 | 250.73 | 272.8196 | 272.8196 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6176.36 | 1419.25 | 1418.05 | 1690.0117 | 249.95 | 271.9617 | 271.9617 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6226.37 | 1419.92 | 1418.72 | 1689.9338 | 249.28 | 271.2138 | 271.2138 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6276.37 | 1420.26 | 1419.06 | 1689.8559 | 248.94 | 270.7959 | 270.7959 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6326.38 | 1420.99 | 1419.79 | 1689.778 | 248.21 | 269.988 | 269.988 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6376.38 | 1421.59 | 1420.39 | 1689.7002 | 247.61 | 269.3102 | 269.3102 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6426.38 | 1421.94 | 1420.74 | 1689.6223 | 247.26 | 268.8823 | 268.8823 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6476.38 | 1422.38 | 1421.18 | 1689.5444 | 246.82 | 268.3644 | 268.3644 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6526.39 | 1423.03 | 1421.83 | 1689.4665 | 246.17 | 267.6365 | 267.6365 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6576.39 | 1423.16 | 1421.96 | 1689.3886 | 246.04 | 267.4286 | 267.4286 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6626.39 | 1423.09 | 1421.89 | 1689.3107 | 246.11 | 267.4207 | 267.4207 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6676.39 | 1423.97 | 1422.77 | 1689.2328 | 245.23 | 266.4628 | 266.4628 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6726.39 | 1423.84 | 1422.64 | 1689.155 | 245.36 | 266.515 | 266.515 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6776.4 | 1424.28 | 1423.08 | 1689.0771 | 244.92 | 265.9971 | 265.9971 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6826.4 | 1424.67 | 1423.47 | 1688.9992 | 244.53 | 265.5292 | 265.5292 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6876.4 | 1424.84 | 1423.64 | 1688.9213 | 244.36 | 265.2813 | 265.2813 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6926.4 | 1424.77 | 1423.57 | 1688.8434 | 244.43 | 265.2734 | 265.2734 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 6976.4 | 1424.9 | 1423.7 | 1688.7655 | 244.3 | 265.0655 | 265.0655 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7026.4 | 1424.45 | 1423.25 | 1688.6876 | 244.75 | 265.4376 | 265.4376 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7076.4 | 1424.59 | 1423.39 | 1688.6098 | 244.61 | 265.2198 | 265.2198 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7126.4 | 1424.76 | 1423.56 | 1688.5319 | 244.44 | 264.9719 | 264.9719 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7176.4 | 1424.59 | 1423.39 | 1688.454 | 244.61 | 265.064 | 265.064 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7226.4 | 1424.85 | 1423.65 | 1688.3761 | 244.35 | 264.7261 | 264.7261 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7276.41 | 1424 | 1422.8 | 1688.2982 | 245.2 | 265.4982 | 265.4982 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7326.41 | 1424.6 | 1423.4 | 1688.2203 | 244.6 | 264.8203 | 264.8203 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7376.41 | 1424.68 | 1423.48 | 1688.1424 | 244.52 | 264.6624 | 264.6624 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7426.42 | 1425.32 | 1424.12 | 1688.0645 | 243.88 | 263.9445 | 263.9445 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7476.42 | 1425.9 | 1424.7 | 1687.9867 | 243.3 | 263.2867 | 263.2867 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7526.42 | 1426.1 | 1424.9 | 1687.9088 | 243.1 | 263.0088 | 263.0088 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7576.43 | 1426.89 | 1425.69 | 1687.8309 | 242.31 | 262.1409 | 262.1409 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7626.43 | 1426.97 | 1425.77 | 1687.753 | 242.23 | 261.983 | 261.983 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7676.43 | 1427.23 | 1426.03 | 1687.6751 | 241.97 | 261.6451 | 261.6451 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7726.43 | 1427.92 | 1426.72 | 1687.5972 | 241.28 | 260.8772 | 260.8772 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7776.43 | 1427.78 | 1426.58 | 1687.5193 | 241.42 | 260.9393 | 260.9393 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7826.43 | 1428.17 | 1426.97 | 1687.4415 | 241.03 | 260.4715 | 260.4715 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7876.43 | 1428.23 | 1427.03 | 1687.3636 | 240.97 | 260.3336 | 260.3336 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7926.43 | 1428.47 | 1427.27 | 1687.2857 | 240.73 | 260.0157 | 260.0157 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 7976.43 | 1428.35 | 1427.15 | 1687.2078 | 240.85 | 260.0578 | 260.0578 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8026.44 | 1428.65 | 1427.45 | 1687.1299 | 240.55 | 259.6799 | 259.6799 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8076.44 | 1429.44 | 1428.24 | 1687.052 | 239.76 | 258.812 | 258.812 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8126.44 | 1429.47 | 1428.27 | 1686.9741 | 239.73 | 258.7041 | 258.7041 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8176.45 | 1428.89 | 1427.69 | 1686.8962 | 240.31 | 259.2062 | 259.2062 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8226.45 | 1428.94 | 1427.74 | 1686.8184 | 240.26 | 259.0784 | 259.0784 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8276.45 | 1428.77 | 1427.57 | 1686.7405 | 240.43 | 259.1705 | 259.1705 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8326.45 | 1429.09 | 1427.89 | 1686.6626 | 240.11 | 258.7726 | 258.7726 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8376.45 | 1429.26 | 1428.06 | 1686.5847 | 239.94 | 258.5247 | 258.5247 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8426.45 | 1428.36 | 1427.16 | 1686.5068 | 240.84 | 259.3468 | 259.3468 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8476.46 | 1428.03 | 1426.83 | 1686.4289 | 241.17 | 259.5989 | 259.5989 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8526.46 | 1427.63 | 1426.43 | 1686.3511 | 241.57 | 259.9211 | 259.9211 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8576.46 | 1427.43 | 1426.23 | 1686.2732 | 241.77 | 260.0432 | 260.0432 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8626.46 | 1427.25 | 1426.05 | 1686.1953 | 241.95 | 260.1453 | 260.1453 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8676.46 | 1427.59 | 1426.39 | 1686.1174 | 241.61 | 259.7274 | 259.7274 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8726.46 | 1427.04 | 1425.84 | 1686.0395 | 242.16 | 260.1995 | 260.1995 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8776.46 | 1427.08 | 1425.88 | 1685.9616 | 242.12 | 260.0816 | 260.0816 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8826.46 | 1427.35 | 1426.15 | 1685.8838 | 241.85 | 259.7338 | 259.7338 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8876.46 | 1427.23 | 1426.03 | 1685.8059 | 241.97 | 259.7759 | 259.7759 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8926.47 | 1427.71 | 1426.51 | 1685.728 | 241.49 | 259.218 | 259.218 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 8976.47 | 1428.1 | 1426.9 | 1685.6501 | 241.1 | 258.7501 | 258.7501 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9026.47 | 1428.86 | 1427.66 | 1685.5722 | 240.34 | 257.9122 | 257.9122 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9076.48 | 1429.55 | 1428.35 | 1685.4943 | 239.65 | 257.1443 | 257.1443 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9126.48 | 1429.71 | 1428.51 | 1685.4164 | 239.49 | 256.9064 | 256.9064 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9176.48 | 1429.55 | 1428.35 | 1685.3385 | 239.65 | 256.9885 | 256.9885 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9226.48 | 1429.91 | 1428.71 | 1685.2607 | 239.29 | 256.5507 | 256.5507 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9276.48 | 1430.21 | 1429.01 | 1685.1828 | 238.99 | 256.1728 | 256.1728 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9326.48 | 1430.45 | 1429.25 | 1685.1049 | 238.75 | 255.8549 | 255.8549 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9376.48 | 1430.33 | 1429.13 | 1685.027 | 238.87 | 255.897 | 255.897 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9426.48 | 1430.23 | 1429.03 | 1684.9491 | 238.97 | 255.9191 | 255.9191 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9476.48 | 1430.08 | 1428.88 | 1684.8712 | 239.12 | 255.9912 | 255.9912 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9526.48 | 1430.26 | 1429.06 | 1684.7934 | 238.94 | 255.7334 | 255.7334 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9576.49 | 1429.35 | 1428.15 | 1684.7155 | 239.85 | 256.5655 | 256.5655 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9626.49 | 1428.97 | 1427.77 | 1684.6376 | 240.23 | 256.8676 | 256.8676 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9676.49 | 1429.29 | 1428.09 | 1684.5597 | 239.91 | 256.4697 | 256.4697 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9726.5 | 1428.43 | 1427.23 | 1684.4818 | 240.77 | 257.2518 | 257.2518 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9776.5 | 1428.09 | 1426.89 | 1684.4039 | 241.11 | 257.5139 | 257.5139 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9826.5 | 1427.97 | 1426.77 | 1684.326 | 241.23 | 257.556 | 257.556 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9876.5 | 1427.85 | 1426.65 | 1684.2481 | 241.35 | 257.5981 | 257.5981 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9926.5 | 1427.67 | 1426.47 | 1684.1703 | 241.53 | 257.7003 | 257.7003 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 9976.5 | 1427.19 | 1425.99 | 1684.0924 | 242.01 | 258.1024 | 258.1024 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10026.51 | 1426.81 | 1425.61 | 1684.0145 | 242.39 | 258.4045 | 258.4045 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10076.51 | 1427.15 | 1425.95 | 1683.9366 | 242.05 | 257.9866 | 257.9866 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10126.52 | 1425.87 | 1424.67 | 1683.8587 | 243.33 | 259.1887 | 259.1887 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10176.52 | 1426.01 | 1424.81 | 1683.7808 | 243.19 | 258.9708 | 258.9708 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10226.52 | 1425.68 | 1424.48 | 1683.7029 | 243.52 | 259.2229 | 259.2229 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10276.53 | 1424.91 | 1423.71 | 1683.625 | 244.29 | 259.915 | 259.915 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10326.53 | 1424.62 | 1423.42 | 1683.5471 | 244.58 | 260.1271 | 260.1271 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10376.53 | 1424.2 | 1423 | 1683.4693 | 245 | 260.4693 | 260.4693 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10426.53 | 1424.48 | 1423.28 | 1683.3914 | 244.72 | 260.1114 | 260.1114 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10476.54 | 1423.48 | 1422.28 | 1683.3135 | 245.72 | 261.0335 | 261.0335 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10526.54 | 1423.17 | 1421.97 | 1683.2356 | 246.03 | 261.2656 | 261.2656 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10576.54 | 1422.95 | 1421.75 | 1683.1577 | 246.25 | 261.4077 | 261.4077 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10626.55 | 1422.74 | 1421.54 | 1683.0798 | 246.46 | 261.5398 | 261.5398 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10676.56 | 1421.48 | 1420.28 | 1683.0019 | 247.72 | 262.7219 | 262.7219 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10726.56 | 1421.5 | 1420.3 | 1682.924 | 247.7 | 262.624 | 262.624 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10776.56 | 1421.52 | 1420.32 | 1682.8461 | 247.68 | 262.5261 | 262.5261 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10826.57 | 1420.52 | 1419.32 | 1682.7682 | 248.68 | 263.4482 | 263.4482 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10876.58 | 1419.9 | 1418.7 | 1682.6904 | 249.3 | 263.9904 | 263.9904 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10926.58 | 1419.82 | 1418.62 | 1682.6125 | 249.38 | 263.9925 | 263.9925 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 10976.58 | 1419.58 | 1418.38 | 1682.5346 | 249.62 | 264.1546 | 264.1546 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11026.58 | 1419.54 | 1418.34 | 1682.4567 | 249.66 | 264.1167 | 264.1167 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11076.58 | 1419.22 | 1418.02 | 1682.3788 | 249.98 | 264.3588 | 264.3588 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11126.58 | 1419.1 | 1417.9 | 1682.3009 | 250.1 | 264.4009 | 264.4009 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11176.58 | 1418.84 | 1417.64 | 1682.2231 | 250.36 | 264.5831 | 264.5831 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11226.58 | 1418.44 | 1417.24 | 1682.1452 | 250.76 | 264.9052 | 264.9052 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11276.61 | 1416.65 | 1415.45 | 1682.0672 | 252.55 | 266.6172 | 266.6172 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11326.61 | 1416.14 | 1414.94 | 1681.9894 | 253.06 | 267.0494 | 267.0494 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11376.62 | 1417.15 | 1415.95 | 1681.9115 | 252.05 | 265.9615 | 265.9615 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11426.62 | 1417.02 | 1415.82 | 1681.8336 | 252.18 | 266.0136 | 266.0136 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11476.63 | 1416.51 | 1415.31 | 1681.7557 | 252.69 | 266.4457 | 266.4457 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11526.64 | 1417.72 | 1416.52 | 1681.6778 | 251.48 | 265.1578 | 265.1578 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11576.65 | 1418.69 | 1417.49 | 1681.5999 | 250.51 | 264.1099 | 264.1099 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11626.65 | 1418.71 | 1417.51 | 1681.522 | 250.49 | 264.012 | 264.012 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11676.65 | 1418.43 | 1417.23 | 1681.4441 | 250.77 | 264.2141 | 264.2141 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11726.65 | 1418.37 | 1417.17 | 1681.3662 | 250.83 | 264.1962 | 264.1962 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11776.65 | 1418.92 | 1417.72 | 1681.2883 | 250.28 | 263.5683 | 263.5683 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11826.66 | 1419.29 | 1418.09 | 1681.2104 | 249.91 | 263.1204 | 263.1204 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11876.66 | 1418.45 | 1417.25 | 1681.1326 | 250.75 | 263.8826 | 263.8826 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11926.67 | 1418.98 | 1417.78 | 1681.0547 | 250.22 | 263.2747 | 263.2747 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 11976.74 | 1421.64 | 1420.44 | 1680.9767 | 247.56 | 260.5367 | 260.5367 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12026.75 | 1422.92 | 1421.72 | 1680.8988 | 246.28 | 259.1788 | 259.1788 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12076.78 | 1424.42 | 1423.22 | 1680.8208 | 244.78 | 257.6008 | 257.6008 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12126.79 | 1425.45 | 1424.25 | 1680.7429 | 243.75 | 256.4929 | 256.4929 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12176.79 | 1426.28 | 1425.08 | 1680.6651 | 242.92 | 255.5851 | 255.5851 | PN30 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12226.82 | 1427.89 | 1426.69 | 1680.5871 | 241.31 | 253.8971 | 253.8971 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12276.84 | 1429.33 | 1428.13 | 1680.5092 | 239.87 | 252.3792 | 252.3792 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12326.85 | 1430.19 | 1428.99 | 1680.4313 | 239.01 | 251.4413 | 251.4413 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12376.87 | 1431.75 | 1430.55 | 1680.3534 | 237.45 | 249.8034 | 249.8034 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12426.88 | 1432.43 | 1431.23 | 1680.2755 | 236.77 | 249.0455 | 249.0455 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12476.89 | 1433.57 | 1432.37 | 1680.1976 | 235.63 | 247.8276 | 247.8276 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12526.91 | 1434.94 | 1433.74 | 1680.1197 | 234.26 | 246.3797 | 246.3797 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12576.93 | 1436.4 | 1435.2 | 1680.0418 | 232.8 | 244.8418 | 244.8418 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12626.94 | 1437.42 | 1436.22 | 1679.9639 | 231.78 | 243.7439 | 243.7439 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12676.95 | 1438.64 | 1437.44 | 1679.886 | 230.56 | 242.446 | 242.446 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12726.96 | 1439.36 | 1438.16 | 1679.8081 | 229.84 | 241.6481 | 241.6481 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12776.97 | 1440.23 | 1439.03 | 1679.7302 | 228.97 | 240.7002 | 240.7002 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12826.97 | 1440.84 | 1439.64 | 1679.6523 | 228.36 | 240.0123 | 240.0123 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12876.99 | 1442.16 | 1440.96 | 1679.5744 | 227.04 | 238.6144 | 238.6144 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12926.99 | 1442.35 | 1441.15 | 1679.4965 | 226.85 | 238.3465 | 238.3465 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 12976.99 | 1443.01 | 1441.81 | 1679.4186 | 226.19 | 237.6086 | 237.6086 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13026.99 | 1443.34 | 1442.14 | 1679.3407 | 225.86 | 237.2007 | 237.2007 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13076.99 | 1443.51 | 1442.31 | 1679.2628 | 225.69 | 236.9528 | 236.9528 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13126.99 | 1443.52 | 1442.32 | 1679.185 | 225.68 | 236.865 | 236.865 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13176.99 | 1443.56 | 1442.36 | 1679.1071 | 225.64 | 236.7471 | 236.7471 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13227 | 1443.04 | 1441.84 | 1679.0292 | 226.16 | 237.1892 | 237.1892 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13277 | 1442.89 | 1441.69 | 1678.9513 | 226.31 | 237.2613 | 237.2613 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13327 | 1442.63 | 1441.43 | 1678.8734 | 226.57 | 237.4434 | 237.4434 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13377 | 1442.67 | 1441.47 | 1678.7955 | 226.53 | 237.3255 | 237.3255 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13427 | 1442.03 | 1440.83 | 1678.7176 | 227.17 | 237.8876 | 237.8876 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13477 | 1441.84 | 1440.64 | 1678.6398 | 227.36 | 237.9998 | 237.9998 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13527 | 1441.54 | 1440.34 | 1678.5619 | 227.66 | 238.2219 | 238.2219 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13577 | 1441.42 | 1440.22 | 1678.484 | 227.78 | 238.264 | 238.264 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13627 | 1441.23 | 1440.03 | 1678.4061 | 227.97 | 238.3761 | 238.3761 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13677 | 1441.26 | 1440.06 | 1678.3282 | 227.94 | 238.2682 | 238.2682 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13727 | 1441.42 | 1440.22 | 1678.2504 | 227.78 | 238.0304 | 238.0304 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13777 | 1441.66 | 1440.46 | 1678.1725 | 227.54 | 237.7125 | 237.7125 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13827 | 1441.64 | 1440.44 | 1678.0946 | 227.56 | 237.6546 | 237.6546 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13877.01 | 1442.35 | 1441.15 | 1678.0167 | 226.85 | 236.8667 | 236.8667 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13927.01 | 1442.44 | 1441.24 | 1677.9388 | 226.76 | 236.6988 | 236.6988 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 13977.01 | 1442.64 | 1441.44 | 1677.8609 | 226.56 | 236.4209 | 236.4209 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14027.01 | 1442.83 | 1441.63 | 1677.783 | 226.37 | 236.153 | 236.153 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14077.01 | 1443.07 | 1441.87 | 1677.7052 | 226.13 | 235.8352 | 235.8352 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14127.01 | 1443.62 | 1442.42 | 1677.6273 | 225.58 | 235.2073 | 235.2073 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14177.02 | 1444.14 | 1442.94 | 1677.5494 | 225.06 | 234.6094 | 234.6094 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14227.02 | 1444.66 | 1443.46 | 1677.4715 | 224.54 | 234.0115 | 234.0115 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14277.02 | 1444.83 | 1443.63 | 1677.3936 | 224.37 | 233.7636 | 233.7636 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14327.02 | 1445.53 | 1444.33 | 1677.3157 | 223.67 | 232.9857 | 232.9857 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14377.03 | 1446.2 | 1445 | 1677.2378 | 223 | 232.2378 | 232.2378 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14427.03 | 1446.46 | 1445.26 | 1677.1599 | 222.74 | 231.8999 | 231.8999 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14477.03 | 1446.97 | 1445.77 | 1677.0821 | 222.23 | 231.3121 | 231.3121 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14527.04 | 1447.66 | 1446.46 | 1677.0042 | 221.54 | 230.5442 | 230.5442 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14577.04 | 1447.96 | 1446.76 | 1676.9263 | 221.24 | 230.1663 | 230.1663 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14627.04 | 1448.22 | 1447.02 | 1676.8484 | 220.98 | 229.8284 | 229.8284 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14677.04 | 1448.71 | 1447.51 | 1676.7705 | 220.49 | 229.2605 | 229.2605 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14727.04 | 1448.76 | 1447.56 | 1676.6926 | 220.44 | 229.1326 | 229.1326 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14777.04 | 1449.15 | 1447.95 | 1676.6147 | 220.05 | 228.6647 | 228.6647 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14827.04 | 1448.84 | 1447.64 | 1676.5369 | 220.36 | 228.8969 | 228.8969 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14877.05 | 1449.37 | 1448.17 | 1676.459 | 219.83 | 228.289 | 228.289 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14927.05 | 1449.58 | 1448.38 | 1676.3811 | 219.62 | 228.0011 | 228.0011 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 14977.05 | 1449.79 | 1448.59 | 1676.3032 | 219.41 | 227.7132 | 227.7132 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15027.05 | 1449.86 | 1448.66 | 1676.2253 | 219.34 | 227.5653 | 227.5653 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15077.05 | 1450.43 | 1449.23 | 1676.1474 | 218.77 | 226.9174 | 226.9174 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15127.05 | 1450.12 | 1448.92 | 1676.0695 | 219.08 | 227.1495 | 227.1495 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15177.05 | 1450.13 | 1448.93 | 1675.9917 | 219.07 | 227.0617 | 227.0617 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15227.05 | 1450.61 | 1449.41 | 1675.9138 | 218.59 | 226.5038 | 226.5038 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15277.05 | 1450.79 | 1449.59 | 1675.8359 | 218.41 | 226.2459 | 226.2459 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15327.05 | 1450.81 | 1449.61 | 1675.758 | 218.39 | 226.148 | 226.148 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15377.05 | 1450.7 | 1449.5 | 1675.6801 | 218.5 | 226.1801 | 226.1801 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15427.06 | 1451.04 | 1449.84 | 1675.6022 | 218.16 | 225.7622 | 225.7622 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15477.06 | 1451.11 | 1449.91 | 1675.5243 | 218.09 | 225.6143 | 225.6143 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15527.06 | 1451.77 | 1450.57 | 1675.4465 | 217.43 | 224.8765 | 224.8765 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15577.06 | 1451.14 | 1449.94 | 1675.3686 | 218.06 | 225.4286 | 225.4286 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15627.06 | 1451.21 | 1450.01 | 1675.2907 | 217.99 | 225.2807 | 225.2807 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15677.07 | 1451.67 | 1450.47 | 1675.2128 | 217.53 | 224.7428 | 224.7428 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15727.07 | 1451.54 | 1450.34 | 1675.1349 | 217.66 | 224.7949 | 224.7949 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15777.07 | 1451.99 | 1450.79 | 1675.057 | 217.21 | 224.267 | 224.267 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15827.07 | 1452.02 | 1450.82 | 1674.9791 | 217.18 | 224.1591 | 224.1591 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15877.07 | 1452.07 | 1450.87 | 1674.9013 | 217.13 | 224.0313 | 224.0313 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15927.07 | 1452.49 | 1451.29 | 1674.8234 | 216.71 | 223.5334 | 223.5334 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 15977.07 | 1452.62 | 1451.42 | 1674.7455 | 216.58 | 223.3255 | 223.3255 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16027.07 | 1452.73 | 1451.53 | 1674.6676 | 216.47 | 223.1376 | 223.1376 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16077.07 | 1452.97 | 1451.77 | 1674.5897 | 216.23 | 222.8197 | 222.8197 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16127.07 | 1452.83 | 1451.63 | 1674.5118 | 216.37 | 222.8818 | 222.8818 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16177.07 | 1452.9 | 1451.7 | 1674.434 | 216.3 | 222.734 | 222.734 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16227.07 | 1452.95 | 1451.75 | 1674.3561 | 216.25 | 222.6061 | 222.6061 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16277.07 | 1452.9 | 1451.7 | 1674.2782 | 216.3 | 222.5782 | 222.5782 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16327.07 | 1452.31 | 1451.11 | 1674.2003 | 216.89 | 223.0903 | 223.0903 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16377.07 | 1452.3 | 1451.1 | 1674.1224 | 216.9 | 223.0224 | 223.0224 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16427.08 | 1451.49 | 1450.29 | 1674.0445 | 217.71 | 223.7545 | 223.7545 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16477.08 | 1451.2 | 1450 | 1673.9666 | 218 | 223.9666 | 223.9666 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16527.08 | 1450.8 | 1449.6 | 1673.8888 | 218.4 | 224.2888 | 224.2888 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16577.08 | 1450.74 | 1449.54 | 1673.8109 | 218.46 | 224.2709 | 224.2709 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16627.09 | 1450.28 | 1449.08 | 1673.733 | 218.92 | 224.653 | 224.653 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16677.09 | 1450.92 | 1449.72 | 1673.6551 | 218.28 | 223.9351 | 223.9351 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16727.09 | 1451.34 | 1450.14 | 1673.5772 | 217.86 | 223.4372 | 223.4372 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16777.11 | 1452.75 | 1451.55 | 1673.4993 | 216.45 | 221.9493 | 221.9493 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16827.11 | 1452.24 | 1451.04 | 1673.4214 | 216.96 | 222.3814 | 222.3814 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16877.12 | 1453.13 | 1451.93 | 1673.3435 | 216.07 | 221.4135 | 221.4135 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16927.14 | 1454.34 | 1453.14 | 1673.2656 | 214.86 | 220.1256 | 220.1256 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 16977.15 | 1455.25 | 1454.05 | 1673.1877 | 213.95 | 219.1377 | 219.1377 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17027.16 | 1456.51 | 1455.31 | 1673.1098 | 212.69 | 217.7998 | 217.7998 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17077.16 | 1456.28 | 1455.08 | 1673.0319 | 212.92 | 217.9519 | 217.9519 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17127.17 | 1457.01 | 1455.81 | 1672.954 | 212.19 | 217.144 | 217.144 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17177.17 | 1457.67 | 1456.47 | 1672.8761 | 211.53 | 216.4061 | 216.4061 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17227.17 | 1457.56 | 1456.36 | 1672.7983 | 211.64 | 216.4383 | 216.4383 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17277.17 | 1458.03 | 1456.83 | 1672.7204 | 211.17 | 215.8904 | 215.8904 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17327.17 | 1458.33 | 1457.13 | 1672.6425 | 210.87 | 215.5125 | 215.5125 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17377.18 | 1458.57 | 1457.37 | 1672.5646 | 210.63 | 215.1946 | 215.1946 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17427.18 | 1459.18 | 1457.98 | 1672.4867 | 210.02 | 214.5067 | 214.5067 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17477.18 | 1459.65 | 1458.45 | 1672.4088 | 209.55 | 213.9588 | 213.9588 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17527.19 | 1460.7 | 1459.5 | 1672.3309 | 208.5 | 212.8309 | 212.8309 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17577.19 | 1460.81 | 1459.61 | 1672.253 | 208.39 | 212.643 | 212.643 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17627.2 | 1461.62 | 1460.42 | 1672.1751 | 207.58 | 211.7551 | 211.7551 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17677.2 | 1462.33 | 1461.13 | 1672.0973 | 206.87 | 210.9673 | 210.9673 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17727.21 | 1462.83 | 1461.63 | 1672.0194 | 206.37 | 210.3894 | 210.3894 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17777.22 | 1463.8 | 1462.6 | 1671.9415 | 205.4 | 209.3415 | 209.3415 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17827.23 | 1464.98 | 1463.78 | 1671.8636 | 204.22 | 208.0836 | 208.0836 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17877.27 | 1466.89 | 1465.69 | 1671.7856 | 202.31 | 206.0956 | 206.0956 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17927.27 | 1467.15 | 1465.95 | 1671.7077 | 202.05 | 205.7577 | 205.7577 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 17977.28 | 1468.41 | 1467.21 | 1671.6298 | 200.79 | 204.4198 | 204.4198 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18027.29 | 1469.5 | 1468.3 | 1671.5519 | 199.7 | 203.2519 | 203.2519 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18077.3 | 1468.98 | 1467.78 | 1671.474 | 200.22 | 203.694 | 203.694 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18127.3 | 1469.59 | 1468.39 | 1671.3962 | 199.61 | 203.0062 | 203.0062 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18177.3 | 1470.1 | 1468.9 | 1671.3183 | 199.1 | 202.4183 | 202.4183 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18227.31 | 1470.88 | 1469.68 | 1671.2404 | 198.32 | 201.5604 | 201.5604 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18277.31 | 1471.61 | 1470.41 | 1671.1625 | 197.59 | 200.7525 | 200.7525 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18327.33 | 1472.71 | 1471.51 | 1671.0846 | 196.49 | 199.5746 | 199.5746 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18377.34 | 1473.96 | 1472.76 | 1671.0067 | 195.24 | 198.2467 | 198.2467 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18427.35 | 1474.5 | 1473.3 | 1670.9288 | 194.7 | 197.6288 | 197.6288 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18477.38 | 1476.31 | 1475.11 | 1670.8508 | 192.89 | 195.7408 | 195.7408 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18527.39 | 1477.26 | 1476.06 | 1670.773 | 191.94 | 194.713 | 194.713 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18577.39 | 1477.66 | 1476.46 | 1670.6951 | 191.54 | 194.2351 | 194.2351 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18627.39 | 1478.19 | 1476.99 | 1670.6172 | 191.01 | 193.6272 | 193.6272 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18670.95 | 1479.22 | 1478.02 | 1670.5493 | 189.98 | 192.5293 | 192.5293 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18721.07 | 1482.67 | 1481.47 | 1670.4713 | 186.53 | 189.0013 | 189.0013 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18771.24 | 1486.74 | 1485.54 | 1670.3931 | 182.46 | 184.8531 | 184.8531 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18821.37 | 1490.37 | 1489.17 | 1670.315 | 178.83 | 181.145 | 181.145 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18871.54 | 1494.5 | 1493.3 | 1670.2369 | 174.7 | 176.9369 | 176.9369 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18921.98 | 1501.16 | 1499.96 | 1670.1583 | 168.04 | 170.1983 | 170.1983 | PN25 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 18972.7 | 1509.64 | 1508.44 | 1670.0793 | 159.56 | 161.6393 | 161.6393 | PN16 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 19024.41 | 1522.84 | 1521.64 | 1669.9988 | 146.36 | 148.3588 | 148.3588 | PN16 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 19408.3 | 1645.96 | 1644.76 | 1669.4008 | 23.24 | 24.6408 | 24.6408 | PN10 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 19428.3 | 1646.42 | 1645.22 | 1669.3696 | 22.78 | 24.1496 | 24.1496 | PN10 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 19448.42 | 1648.63 | 1647.43 | 1669.3383 | 20.57 | 21.9083 | 21.9083 | PN10 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 19468.45 | 1649.59 | 1648.39 | 1669.3071 | 19.61 | 20.9171 | 20.9171 | PN10 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 19480.19 | 1649.7 | 1648.5 | 1669.2888 | 19.5 | 20.7888 | 20.7888 | PN10 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 19512.89 | 1646.52 | 1645.32 | 1669.2379 | 22.68 | 23.9179 | 23.9179 | PN10 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 19542.37 | 1649.65 | 1648.45 | 1669.192 | 19.55 | 20.742 | 20.742 | PN10 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 19589.57 | 1655.69 | 1654.49 | 1669.1184 | 13.51 | 14.6284 | 14.6284 | PN10 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 19645.61 | 1661.36 | 1660.16 | 1669.0311 | 7.84 | 8.8711 | 8.8711 | PN10 | OK | yes
Z4 WTP-Ikana | WTP_IKANA_RM | 19665.64 | 1662.58 | 1661.38 | 1668.9999 | 6.62 | 7.6199 | 7.6199 | PN10 | end at tank | no
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 0 | 1662.58 | 1661.38 | 1663.3 | 6.62 | 1.92 | 6.62 | PN10 | end at tank | no
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 170.33 | 1579.17 | 1577.97 | 1663.0742 | 90.03 | 85.1042 | 90.03 | PN10 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 225.08 | 1555.04 | 1553.84 | 1663.0016 | 114.16 | 109.1616 | 114.16 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 278 | 1537.7 | 1536.5 | 1662.9314 | 131.5 | 126.4314 | 131.5 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 328.96 | 1522.84 | 1521.64 | 1662.8639 | 146.36 | 141.2239 | 146.36 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 380.56 | 1510.1 | 1508.9 | 1662.7954 | 159.1 | 153.8954 | 159.1 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 431.14 | 1502.46 | 1501.26 | 1662.7284 | 166.74 | 161.4684 | 166.74 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 481.46 | 1496.78 | 1495.58 | 1662.6617 | 172.42 | 167.0817 | 172.42 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 531.85 | 1490.49 | 1489.29 | 1662.5949 | 178.71 | 173.3049 | 178.71 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 581.99 | 1486.84 | 1485.64 | 1662.5284 | 182.36 | 176.8884 | 182.36 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 632.16 | 1482.69 | 1481.49 | 1662.4619 | 186.51 | 180.9719 | 186.51 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 682.25 | 1479.62 | 1478.42 | 1662.3954 | 189.58 | 183.9754 | 189.58 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 721.28 | 1480.19 | 1478.99 | 1662.3437 | 189.01 | 183.3537 | 189.01 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 771.29 | 1481.29 | 1480.09 | 1662.2774 | 187.91 | 182.1874 | 187.91 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 821.3 | 1482.18 | 1480.98 | 1662.2111 | 187.02 | 181.2311 | 187.02 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 871.3 | 1482.82 | 1481.62 | 1662.1448 | 186.38 | 180.5248 | 186.38 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 915.78 | 1482.8 | 1481.6 | 1662.0858 | 186.4 | 180.4858 | 186.4 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 965.84 | 1480.39 | 1479.19 | 1662.0195 | 188.81 | 182.8295 | 188.81 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1009.13 | 1477.15 | 1475.95 | 1661.9621 | 192.05 | 186.0121 | 192.05 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1059.16 | 1475.43 | 1474.23 | 1661.8957 | 193.77 | 187.6657 | 193.77 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1109.22 | 1472.93 | 1471.73 | 1661.8294 | 196.27 | 190.0994 | 196.27 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1159.24 | 1471.75 | 1470.55 | 1661.763 | 197.45 | 191.213 | 197.45 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1209.26 | 1470.11 | 1468.91 | 1661.6967 | 199.09 | 192.7867 | 199.09 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1259.3 | 1468.25 | 1467.05 | 1661.6304 | 200.95 | 194.5804 | 200.95 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1309.31 | 1467.1 | 1465.9 | 1661.5641 | 202.1 | 195.6641 | 202.1 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1359.33 | 1465.95 | 1464.75 | 1661.4978 | 203.25 | 196.7478 | 203.25 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1409.34 | 1464.72 | 1463.52 | 1661.4314 | 204.48 | 197.9114 | 204.48 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1459.36 | 1463.52 | 1462.32 | 1661.3651 | 205.68 | 199.0451 | 205.68 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1509.39 | 1461.76 | 1460.56 | 1661.2988 | 207.44 | 200.7388 | 207.44 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1559.4 | 1460.69 | 1459.49 | 1661.2325 | 208.51 | 201.7425 | 208.51 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1609.42 | 1459.34 | 1458.14 | 1661.1662 | 209.86 | 203.0262 | 209.86 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1659.42 | 1458.97 | 1457.77 | 1661.0999 | 210.23 | 203.3299 | 210.23 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1709.43 | 1457.77 | 1456.57 | 1661.0336 | 211.43 | 204.4636 | 211.43 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1759.44 | 1457.01 | 1455.81 | 1660.9673 | 212.19 | 205.1573 | 212.19 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1809.44 | 1456.65 | 1455.45 | 1660.901 | 212.55 | 205.451 | 212.55 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1859.44 | 1457.33 | 1456.13 | 1660.8347 | 211.87 | 204.7047 | 211.87 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1909.46 | 1456.05 | 1454.85 | 1660.7684 | 213.15 | 205.9184 | 213.15 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 1959.46 | 1456.18 | 1454.98 | 1660.7021 | 213.02 | 205.7221 | 213.02 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2009.46 | 1456.26 | 1455.06 | 1660.6358 | 212.94 | 205.5758 | 212.94 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2059.46 | 1456.49 | 1455.29 | 1660.5695 | 212.71 | 205.2795 | 212.71 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2109.46 | 1456.29 | 1455.09 | 1660.5032 | 212.91 | 205.4132 | 212.91 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2159.46 | 1456.23 | 1455.03 | 1660.4369 | 212.97 | 205.4069 | 212.97 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2209.47 | 1457.11 | 1455.91 | 1660.3706 | 212.09 | 204.4606 | 212.09 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2259.47 | 1457.1 | 1455.9 | 1660.3043 | 212.1 | 204.4043 | 212.1 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2309.48 | 1458.05 | 1456.85 | 1660.238 | 211.15 | 203.388 | 211.15 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2359.48 | 1458.72 | 1457.52 | 1660.1717 | 210.48 | 202.6517 | 210.48 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2409.48 | 1459.22 | 1458.02 | 1660.1054 | 209.98 | 202.0854 | 209.98 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2459.49 | 1459.83 | 1458.63 | 1660.0391 | 209.37 | 201.4091 | 209.37 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2509.49 | 1459.77 | 1458.57 | 1659.9728 | 209.43 | 201.4028 | 209.43 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2559.49 | 1460.05 | 1458.85 | 1659.9065 | 209.15 | 201.0565 | 209.15 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2609.49 | 1460.41 | 1459.21 | 1659.8402 | 208.79 | 200.6302 | 208.79 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2659.49 | 1459.92 | 1458.72 | 1659.774 | 209.28 | 201.054 | 209.28 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2709.49 | 1459.75 | 1458.55 | 1659.7077 | 209.45 | 201.1577 | 209.45 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2759.5 | 1459.06 | 1457.86 | 1659.6414 | 210.14 | 201.7814 | 210.14 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2809.5 | 1459.48 | 1458.28 | 1659.5751 | 209.72 | 201.2951 | 209.72 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2859.51 | 1458.44 | 1457.24 | 1659.5088 | 210.76 | 202.2688 | 210.76 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2906.15 | 1457.89 | 1456.69 | 1659.4469 | 211.31 | 202.7569 | 211.31 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 2956.16 | 1458.35 | 1457.15 | 1659.3806 | 210.85 | 202.2306 | 210.85 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3006.16 | 1458.6 | 1457.4 | 1659.3143 | 210.6 | 201.9143 | 210.6 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3056.16 | 1458.48 | 1457.28 | 1659.248 | 210.72 | 201.968 | 210.72 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3106.16 | 1458.45 | 1457.25 | 1659.1817 | 210.75 | 201.9317 | 210.75 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3156.16 | 1458.37 | 1457.17 | 1659.1155 | 210.83 | 201.9455 | 210.83 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3206.16 | 1458.6 | 1457.4 | 1659.0492 | 210.6 | 201.6492 | 210.6 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3256.16 | 1458.6 | 1457.4 | 1658.9829 | 210.6 | 201.5829 | 210.6 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3306.16 | 1458.8 | 1457.6 | 1658.9166 | 210.4 | 201.3166 | 210.4 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3356.16 | 1459.03 | 1457.83 | 1658.8503 | 210.17 | 201.0203 | 210.17 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3406.16 | 1459.58 | 1458.38 | 1658.784 | 209.62 | 200.404 | 209.62 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3456.16 | 1459.82 | 1458.62 | 1658.7177 | 209.38 | 200.0977 | 209.38 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3506.16 | 1460.21 | 1459.01 | 1658.6514 | 208.99 | 199.6414 | 208.99 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3556.16 | 1460.3 | 1459.1 | 1658.5851 | 208.9 | 199.4851 | 208.9 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3606.16 | 1460.55 | 1459.35 | 1658.5188 | 208.65 | 199.1688 | 208.65 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3656.16 | 1460.7 | 1459.5 | 1658.4525 | 208.5 | 198.9525 | 208.5 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3706.16 | 1461.01 | 1459.81 | 1658.3862 | 208.19 | 198.5762 | 208.19 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3756.17 | 1461.4 | 1460.2 | 1658.3199 | 207.8 | 198.1199 | 207.8 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3806.17 | 1461.45 | 1460.25 | 1658.2536 | 207.75 | 198.0036 | 207.75 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3856.17 | 1462.07 | 1460.87 | 1658.1874 | 207.13 | 197.3174 | 207.13 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3906.17 | 1462.46 | 1461.26 | 1658.1211 | 206.74 | 196.8611 | 206.74 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 3956.17 | 1462.99 | 1461.79 | 1658.0548 | 206.21 | 196.2648 | 206.21 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4006.18 | 1463.64 | 1462.44 | 1657.9885 | 205.56 | 195.5485 | 205.56 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4056.19 | 1464.46 | 1463.26 | 1657.9222 | 204.74 | 194.6622 | 204.74 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4106.19 | 1464.83 | 1463.63 | 1657.8559 | 204.37 | 194.2259 | 204.37 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4156.19 | 1465.58 | 1464.38 | 1657.7896 | 203.62 | 193.4096 | 203.62 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4206.2 | 1466.45 | 1465.25 | 1657.7233 | 202.75 | 192.4733 | 202.75 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4256.2 | 1466.97 | 1465.77 | 1657.657 | 202.23 | 191.887 | 202.23 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4306.2 | 1467.05 | 1465.85 | 1657.5907 | 202.15 | 191.7407 | 202.15 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4356.2 | 1467.42 | 1466.22 | 1657.5244 | 201.78 | 191.3044 | 201.78 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4406.24 | 1469.29 | 1468.09 | 1657.458 | 199.91 | 189.368 | 199.91 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4456.25 | 1468.42 | 1467.22 | 1657.3917 | 200.78 | 190.1717 | 200.78 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4506.25 | 1468.97 | 1467.77 | 1657.3255 | 200.23 | 189.5555 | 200.23 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4556.25 | 1469.46 | 1468.26 | 1657.2592 | 199.74 | 188.9992 | 199.74 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4606.26 | 1470.29 | 1469.09 | 1657.1929 | 198.91 | 188.1029 | 198.91 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4656.27 | 1471.41 | 1470.21 | 1657.1266 | 197.79 | 186.9166 | 197.79 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4706.28 | 1472.39 | 1471.19 | 1657.0602 | 196.81 | 185.8702 | 196.81 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4756.29 | 1473.49 | 1472.29 | 1656.9939 | 195.71 | 184.7039 | 195.71 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4806.3 | 1474.44 | 1473.24 | 1656.9276 | 194.76 | 183.6876 | 194.76 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4856.32 | 1475.64 | 1474.44 | 1656.8613 | 193.56 | 182.4213 | 193.56 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4906.34 | 1477.18 | 1475.98 | 1656.795 | 192.02 | 180.815 | 192.02 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 4956.36 | 1478.7 | 1477.5 | 1656.7287 | 190.5 | 179.2287 | 190.5 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5006.4 | 1480.49 | 1479.29 | 1656.6623 | 188.71 | 177.3723 | 188.71 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5056.41 | 1481.55 | 1480.35 | 1656.596 | 187.65 | 176.246 | 187.65 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5106.44 | 1483.24 | 1482.04 | 1656.5297 | 185.96 | 174.4897 | 185.96 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5156.45 | 1484.43 | 1483.23 | 1656.4634 | 184.77 | 173.2334 | 184.77 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5206.46 | 1485.66 | 1484.46 | 1656.3971 | 183.54 | 171.9371 | 183.54 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5256.46 | 1485.65 | 1484.45 | 1656.3308 | 183.55 | 171.8808 | 183.55 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5306.47 | 1484.99 | 1483.79 | 1656.2645 | 184.21 | 172.4745 | 184.21 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5356.47 | 1484.65 | 1483.45 | 1656.1982 | 184.55 | 172.7482 | 184.55 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5406.48 | 1483.5 | 1482.3 | 1656.1319 | 185.7 | 173.8319 | 185.7 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5456.51 | 1481.82 | 1480.62 | 1656.0656 | 187.38 | 175.4456 | 187.38 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5506.51 | 1482.1 | 1480.9 | 1655.9993 | 187.1 | 175.0993 | 187.1 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5556.52 | 1481.05 | 1479.85 | 1655.933 | 188.15 | 176.083 | 188.15 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5606.52 | 1480.83 | 1479.63 | 1655.8667 | 188.37 | 176.2367 | 188.37 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5656.52 | 1480.85 | 1479.65 | 1655.8004 | 188.35 | 176.1504 | 188.35 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5706.52 | 1480.72 | 1479.52 | 1655.7341 | 188.48 | 176.2141 | 188.48 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5756.53 | 1481.29 | 1480.09 | 1655.6678 | 187.91 | 175.5778 | 187.91 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5806.53 | 1481.56 | 1480.36 | 1655.6015 | 187.64 | 175.2415 | 187.64 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5856.53 | 1481.89 | 1480.69 | 1655.5352 | 187.31 | 174.8452 | 187.31 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5906.56 | 1483.52 | 1482.32 | 1655.4689 | 185.68 | 173.1489 | 185.68 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 5956.56 | 1483.38 | 1482.18 | 1655.4026 | 185.82 | 173.2226 | 185.82 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6006.56 | 1483.63 | 1482.43 | 1655.3363 | 185.57 | 172.9063 | 185.57 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6056.57 | 1484.61 | 1483.41 | 1655.27 | 184.59 | 171.86 | 184.59 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6106.58 | 1485.91 | 1484.71 | 1655.2037 | 183.29 | 170.4937 | 183.29 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6156.58 | 1485.57 | 1484.37 | 1655.1374 | 183.63 | 170.7674 | 183.63 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6206.6 | 1486.66 | 1485.46 | 1655.0711 | 182.54 | 169.6111 | 182.54 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6256.6 | 1487.43 | 1486.23 | 1655.0048 | 181.77 | 168.7748 | 181.77 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6306.63 | 1489.02 | 1487.82 | 1654.9384 | 180.18 | 167.1184 | 180.18 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6356.64 | 1490.06 | 1488.86 | 1654.8721 | 179.14 | 166.0121 | 179.14 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6406.64 | 1490.86 | 1489.66 | 1654.8058 | 178.34 | 165.1458 | 178.34 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6456.66 | 1492.22 | 1491.02 | 1654.7395 | 176.98 | 163.7195 | 176.98 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6506.72 | 1494.65 | 1493.45 | 1654.6732 | 174.55 | 161.2232 | 174.55 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6556.72 | 1494.47 | 1493.27 | 1654.6069 | 174.73 | 161.3369 | 174.73 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6606.76 | 1496.36 | 1495.16 | 1654.5405 | 172.84 | 159.3805 | 172.84 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6656.78 | 1497.9 | 1496.7 | 1654.4742 | 171.3 | 157.7742 | 171.3 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6706.97 | 1498.72 | 1497.52 | 1654.4077 | 170.48 | 156.8877 | 170.48 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6757.06 | 1501.7 | 1500.5 | 1654.3412 | 167.5 | 153.8412 | 167.5 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6807.09 | 1499.98 | 1498.78 | 1654.2749 | 169.22 | 155.4949 | 169.22 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6857.1 | 1501.05 | 1499.85 | 1654.2086 | 168.15 | 154.3586 | 168.15 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6907.1 | 1501.49 | 1500.29 | 1654.1423 | 167.71 | 153.8523 | 167.71 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 6957.11 | 1502.22 | 1501.02 | 1654.076 | 166.98 | 153.056 | 166.98 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7007.12 | 1503.31 | 1502.11 | 1654.0097 | 165.89 | 151.8997 | 165.89 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7057.12 | 1503.27 | 1502.07 | 1653.9434 | 165.93 | 151.8734 | 165.93 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7107.13 | 1504.21 | 1503.01 | 1653.8771 | 164.99 | 150.8671 | 164.99 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7157.15 | 1505.7 | 1504.5 | 1653.8108 | 163.5 | 149.3108 | 163.5 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7207.15 | 1506 | 1504.8 | 1653.7445 | 163.2 | 148.9445 | 163.2 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7257.16 | 1507.06 | 1505.86 | 1653.6782 | 162.14 | 147.8182 | 162.14 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7307.16 | 1506.71 | 1505.51 | 1653.6119 | 162.49 | 148.1019 | 162.49 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7357.17 | 1507.4 | 1506.2 | 1653.5456 | 161.8 | 147.3456 | 161.8 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7407.17 | 1507.29 | 1506.09 | 1653.4793 | 161.91 | 147.3893 | 161.91 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7457.17 | 1507.59 | 1506.39 | 1653.413 | 161.61 | 147.023 | 161.61 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7507.17 | 1508.12 | 1506.92 | 1653.3467 | 161.08 | 146.4267 | 161.08 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7557.17 | 1508.77 | 1507.57 | 1653.2804 | 160.43 | 145.7104 | 160.43 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7607.18 | 1509.48 | 1508.28 | 1653.2141 | 159.72 | 144.9341 | 159.72 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7657.18 | 1509.61 | 1508.41 | 1653.1478 | 159.59 | 144.7378 | 159.59 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7707.23 | 1511.87 | 1510.67 | 1653.0815 | 157.33 | 142.4115 | 157.33 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7757.03 | 1514 | 1512.8 | 1653.0155 | 155.2 | 140.2155 | 155.2 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7807.04 | 1515.05 | 1513.85 | 1652.9491 | 154.15 | 139.0991 | 154.15 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7855.04 | 1517.52 | 1516.32 | 1652.8855 | 151.68 | 136.5655 | 151.68 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7905.14 | 1520.66 | 1519.46 | 1652.8191 | 148.54 | 133.3591 | 148.54 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 7955.14 | 1520.87 | 1519.67 | 1652.7528 | 148.33 | 133.0828 | 148.33 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8005.14 | 1520.46 | 1519.26 | 1652.6865 | 148.74 | 133.4265 | 148.74 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8055.14 | 1520.42 | 1519.22 | 1652.6202 | 148.78 | 133.4002 | 148.78 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8105.14 | 1520.61 | 1519.41 | 1652.5539 | 148.59 | 133.1439 | 148.59 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8155.25 | 1519.72 | 1518.52 | 1652.4875 | 149.48 | 133.9675 | 149.48 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8205.27 | 1518.39 | 1517.19 | 1652.4212 | 150.81 | 135.2312 | 150.81 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8255.28 | 1517.52 | 1516.32 | 1652.3549 | 151.68 | 136.0349 | 151.68 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8305.28 | 1517.22 | 1516.02 | 1652.2886 | 151.98 | 136.2686 | 151.98 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8355.28 | 1517.15 | 1515.95 | 1652.2223 | 152.05 | 136.2723 | 152.05 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8405.28 | 1517.31 | 1516.11 | 1652.156 | 151.89 | 136.046 | 151.89 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8455.28 | 1517.41 | 1516.21 | 1652.0897 | 151.79 | 135.8797 | 151.79 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8505.28 | 1517.61 | 1516.41 | 1652.0234 | 151.59 | 135.6134 | 151.59 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8555.29 | 1518.88 | 1517.68 | 1651.9571 | 150.32 | 134.2771 | 150.32 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8605.3 | 1519.79 | 1518.59 | 1651.8908 | 149.41 | 133.3008 | 149.41 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8655.32 | 1521.15 | 1519.95 | 1651.8245 | 148.05 | 131.8745 | 148.05 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8705.33 | 1522.18 | 1520.98 | 1651.7582 | 147.02 | 130.7782 | 147.02 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8755.33 | 1522.74 | 1521.54 | 1651.6919 | 146.46 | 130.1519 | 146.46 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8805.34 | 1523.46 | 1522.26 | 1651.6256 | 145.74 | 129.3656 | 145.74 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8855.34 | 1523.19 | 1521.99 | 1651.5593 | 146.01 | 129.5693 | 146.01 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8905.34 | 1522.99 | 1521.79 | 1651.493 | 146.21 | 129.703 | 146.21 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 8955.36 | 1521.71 | 1520.51 | 1651.4267 | 147.49 | 130.9167 | 147.49 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9005.37 | 1520.39 | 1519.19 | 1651.3604 | 148.81 | 132.1704 | 148.81 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9055.41 | 1518.55 | 1517.35 | 1651.294 | 150.65 | 133.944 | 150.65 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9105.44 | 1516.79 | 1515.59 | 1651.2277 | 152.41 | 135.6377 | 152.41 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9155.48 | 1514.82 | 1513.62 | 1651.1613 | 154.38 | 137.5413 | 154.38 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9205.51 | 1513.02 | 1511.82 | 1651.095 | 156.18 | 139.275 | 156.18 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9255.57 | 1510.65 | 1509.45 | 1651.0286 | 158.55 | 141.5786 | 158.55 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9305.59 | 1509.18 | 1507.98 | 1650.9623 | 160.02 | 142.9823 | 160.02 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9355.59 | 1508.49 | 1507.29 | 1650.896 | 160.71 | 143.606 | 160.71 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9405.6 | 1507.63 | 1506.43 | 1650.8297 | 161.57 | 144.3997 | 161.57 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9455.61 | 1506.52 | 1505.32 | 1650.7634 | 162.68 | 145.4434 | 162.68 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9505.61 | 1506.7 | 1505.5 | 1650.6971 | 162.5 | 145.1971 | 162.5 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9555.61 | 1506.53 | 1505.33 | 1650.6308 | 162.67 | 145.3008 | 162.67 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9605.61 | 1506.39 | 1505.19 | 1650.5645 | 162.81 | 145.3745 | 162.81 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9655.61 | 1506.78 | 1505.58 | 1650.4982 | 162.42 | 144.9182 | 162.42 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9705.61 | 1506.75 | 1505.55 | 1650.432 | 162.45 | 144.882 | 162.45 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9755.6 | 1506.97 | 1505.77 | 1650.3657 | 162.23 | 144.5957 | 162.23 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9805.61 | 1506.36 | 1505.16 | 1650.2994 | 162.84 | 145.1394 | 162.84 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9855.61 | 1506.26 | 1505.06 | 1650.2331 | 162.94 | 145.1731 | 162.94 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9905.61 | 1506.46 | 1505.26 | 1650.1668 | 162.74 | 144.9068 | 162.74 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 9955.61 | 1505.88 | 1504.68 | 1650.1005 | 163.32 | 145.4205 | 163.32 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10005.61 | 1506.2 | 1505 | 1650.0342 | 163 | 145.0342 | 163 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10055.61 | 1506.39 | 1505.19 | 1649.9679 | 162.81 | 144.7779 | 162.81 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10105.61 | 1506.72 | 1505.52 | 1649.9016 | 162.48 | 144.3816 | 162.48 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10155.62 | 1507.46 | 1506.26 | 1649.8353 | 161.74 | 143.5753 | 161.74 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10205.62 | 1508.08 | 1506.88 | 1649.769 | 161.12 | 142.889 | 161.12 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10255.62 | 1508.29 | 1507.09 | 1649.7027 | 160.91 | 142.6127 | 160.91 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10305.63 | 1508.91 | 1507.71 | 1649.6364 | 160.29 | 141.9264 | 160.29 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10355.64 | 1509.82 | 1508.62 | 1649.5701 | 159.38 | 140.9501 | 159.38 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10405.64 | 1510.06 | 1508.86 | 1649.5038 | 159.14 | 140.6438 | 159.14 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10455.64 | 1510.6 | 1509.4 | 1649.4375 | 158.6 | 140.0375 | 158.6 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10505.64 | 1510.64 | 1509.44 | 1649.3712 | 158.56 | 139.9312 | 158.56 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10555.64 | 1510.22 | 1509.02 | 1649.305 | 158.98 | 140.285 | 158.98 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10605.65 | 1509.19 | 1507.99 | 1649.2387 | 160.01 | 141.2487 | 160.01 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10655.66 | 1508.47 | 1507.27 | 1649.1723 | 160.73 | 141.9023 | 160.73 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10705.68 | 1507.05 | 1505.85 | 1649.106 | 162.15 | 143.256 | 162.15 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10755.69 | 1506.02 | 1504.82 | 1649.0397 | 163.18 | 144.2197 | 163.18 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10805.7 | 1504.75 | 1503.55 | 1648.9734 | 164.45 | 145.4234 | 164.45 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10855.73 | 1503.07 | 1501.87 | 1648.9071 | 166.13 | 147.0371 | 166.13 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10905.75 | 1501.64 | 1500.44 | 1648.8408 | 167.56 | 148.4008 | 167.56 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 10955.78 | 1500.02 | 1498.82 | 1648.7744 | 169.18 | 149.9544 | 169.18 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11005.78 | 1499.36 | 1498.16 | 1648.7081 | 169.84 | 150.5481 | 169.84 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11055.83 | 1497.28 | 1496.08 | 1648.6418 | 171.92 | 152.5618 | 171.92 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11105.83 | 1496.52 | 1495.32 | 1648.5755 | 172.68 | 153.2555 | 172.68 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11155.97 | 1492.75 | 1491.55 | 1648.509 | 176.45 | 156.959 | 176.45 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11206.04 | 1495.3 | 1494.1 | 1648.4426 | 173.9 | 154.3426 | 173.9 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11256.04 | 1495.95 | 1494.75 | 1648.3763 | 173.25 | 153.6263 | 173.25 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11306.04 | 1496.1 | 1494.9 | 1648.31 | 173.1 | 153.41 | 173.1 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11356.05 | 1496.59 | 1495.39 | 1648.2437 | 172.61 | 152.8537 | 172.61 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11406.05 | 1496.19 | 1494.99 | 1648.1775 | 173.01 | 153.1875 | 173.01 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11456.07 | 1497.77 | 1496.57 | 1648.1111 | 171.43 | 151.5411 | 171.43 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11506.07 | 1497.7 | 1496.5 | 1648.0448 | 171.5 | 151.5448 | 171.5 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11556.07 | 1497.94 | 1496.74 | 1647.9786 | 171.26 | 151.2386 | 171.26 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11606.07 | 1497.86 | 1496.66 | 1647.9123 | 171.34 | 151.2523 | 171.34 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11656.08 | 1497.17 | 1495.97 | 1647.846 | 172.03 | 151.876 | 172.03 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11706.08 | 1496.71 | 1495.51 | 1647.7797 | 172.49 | 152.2697 | 172.49 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11756.08 | 1496.21 | 1495.01 | 1647.7134 | 172.99 | 152.7034 | 172.99 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11806.09 | 1497.06 | 1495.86 | 1647.6471 | 172.14 | 151.7871 | 172.14 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11856.1 | 1495.92 | 1494.72 | 1647.5808 | 173.28 | 152.8608 | 173.28 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11906.1 | 1495.83 | 1494.63 | 1647.5145 | 173.37 | 152.8845 | 173.37 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 11956.11 | 1496.28 | 1495.08 | 1647.4482 | 172.92 | 152.3682 | 172.92 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12006.11 | 1495.38 | 1494.18 | 1647.3819 | 173.82 | 153.2019 | 173.82 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12056.12 | 1494.83 | 1493.63 | 1647.3156 | 174.37 | 153.6856 | 174.37 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12106.13 | 1493.9 | 1492.7 | 1647.2493 | 175.3 | 154.5493 | 175.3 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12156.14 | 1492.72 | 1491.52 | 1647.183 | 176.48 | 155.663 | 176.48 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12206.16 | 1491.37 | 1490.17 | 1647.1166 | 177.83 | 156.9466 | 177.83 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12256.22 | 1489.16 | 1487.96 | 1647.0503 | 180.04 | 159.0903 | 180.04 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12306.25 | 1487.37 | 1486.17 | 1646.9839 | 181.83 | 160.8139 | 181.83 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12356.4 | 1491.24 | 1490.04 | 1646.9174 | 177.96 | 156.8774 | 177.96 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12406.44 | 1493.32 | 1492.12 | 1646.8511 | 175.88 | 154.7311 | 175.88 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12456.5 | 1495.81 | 1494.61 | 1646.7847 | 173.39 | 152.1747 | 173.39 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12506.57 | 1498.33 | 1497.13 | 1646.7183 | 170.87 | 149.5883 | 170.87 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12556.63 | 1500.75 | 1499.55 | 1646.652 | 168.45 | 147.102 | 168.45 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12606.7 | 1503.49 | 1502.29 | 1646.5856 | 165.71 | 144.2956 | 165.71 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12656.72 | 1504.89 | 1503.69 | 1646.5193 | 164.31 | 142.8293 | 164.31 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12706.77 | 1507.04 | 1505.84 | 1646.4529 | 162.16 | 140.6129 | 162.16 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12756.79 | 1508.67 | 1507.47 | 1646.3866 | 160.53 | 138.9166 | 160.53 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12806.83 | 1510.53 | 1509.33 | 1646.3202 | 158.67 | 136.9902 | 158.67 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12856.85 | 1511.89 | 1510.69 | 1646.2539 | 157.31 | 135.5639 | 157.31 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12906.86 | 1513.15 | 1511.95 | 1646.1876 | 156.05 | 134.2376 | 156.05 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 12956.87 | 1513.76 | 1512.56 | 1646.1213 | 155.44 | 133.5613 | 155.44 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13006.87 | 1514.19 | 1512.99 | 1646.055 | 155.01 | 133.065 | 155.01 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13056.87 | 1513.97 | 1512.77 | 1645.9887 | 155.23 | 133.2187 | 155.23 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13106.87 | 1513.35 | 1512.15 | 1645.9224 | 155.85 | 133.7724 | 155.85 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13156.88 | 1512.72 | 1511.52 | 1645.8561 | 156.48 | 134.3361 | 156.48 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13206.93 | 1510.49 | 1509.29 | 1645.7898 | 158.71 | 136.4998 | 158.71 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13256.8 | 1508.99 | 1507.79 | 1645.7237 | 160.21 | 137.9337 | 160.21 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13306.86 | 1506.45 | 1505.25 | 1645.6573 | 162.75 | 140.4073 | 162.75 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13356.89 | 1504.91 | 1503.71 | 1645.591 | 164.29 | 141.881 | 164.29 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13406.95 | 1502.4 | 1501.2 | 1645.5246 | 166.8 | 144.3246 | 166.8 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13457.04 | 1499.33 | 1498.13 | 1645.4582 | 169.87 | 147.3282 | 169.87 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13507.07 | 1497.68 | 1496.48 | 1645.3918 | 171.52 | 148.9118 | 171.52 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13557.12 | 1495.35 | 1494.15 | 1645.3255 | 173.85 | 151.1755 | 173.85 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13607.16 | 1493.52 | 1492.32 | 1645.2591 | 175.68 | 152.9391 | 175.68 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13657.2 | 1491.44 | 1490.24 | 1645.1928 | 177.76 | 154.9528 | 177.76 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13707.24 | 1489.48 | 1488.28 | 1645.1265 | 179.72 | 156.8465 | 179.72 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13757.42 | 1485.19 | 1483.99 | 1645.0599 | 184.01 | 161.0699 | 184.01 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13807.49 | 1482.67 | 1481.47 | 1644.9935 | 186.53 | 163.5235 | 186.53 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13857.62 | 1486.35 | 1485.15 | 1644.9271 | 182.85 | 159.7771 | 182.85 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13907.67 | 1488.62 | 1487.42 | 1644.8607 | 180.58 | 157.4407 | 180.58 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 13957.7 | 1490.13 | 1488.93 | 1644.7944 | 179.07 | 155.8644 | 179.07 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14007.73 | 1492.05 | 1490.85 | 1644.7281 | 177.15 | 153.8781 | 177.15 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14057.79 | 1494.42 | 1493.22 | 1644.6617 | 174.78 | 151.4417 | 174.78 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14107.8 | 1495.46 | 1494.26 | 1644.5954 | 173.74 | 150.3354 | 173.74 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14157.86 | 1497.84 | 1496.64 | 1644.529 | 171.36 | 147.889 | 171.36 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14207.92 | 1500.31 | 1499.11 | 1644.4626 | 168.89 | 145.3526 | 168.89 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14257.96 | 1502.43 | 1501.23 | 1644.3963 | 166.77 | 143.1663 | 166.77 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14308.04 | 1505.19 | 1503.99 | 1644.3299 | 164.01 | 140.3399 | 164.01 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14358.08 | 1507.31 | 1506.11 | 1644.2635 | 161.89 | 138.1535 | 161.89 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14408.12 | 1509.23 | 1508.03 | 1644.1972 | 159.97 | 136.1672 | 159.97 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14458.15 | 1510.97 | 1509.77 | 1644.1309 | 158.23 | 134.3609 | 158.23 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14508.19 | 1512.99 | 1511.79 | 1644.0645 | 156.21 | 132.2745 | 156.21 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14558.21 | 1514.39 | 1513.19 | 1643.9982 | 154.81 | 130.8082 | 154.81 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14608.23 | 1515.68 | 1514.48 | 1643.9319 | 153.52 | 129.4519 | 153.52 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14658.23 | 1516.2 | 1515 | 1643.8656 | 153 | 128.8656 | 153 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14708.23 | 1516.33 | 1515.13 | 1643.7993 | 152.87 | 128.6693 | 152.87 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14758.23 | 1516.4 | 1515.2 | 1643.733 | 152.8 | 128.533 | 152.8 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14808.25 | 1515.58 | 1514.38 | 1643.6667 | 153.62 | 129.2867 | 153.62 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14858.25 | 1514.99 | 1513.79 | 1643.6004 | 154.21 | 129.8104 | 154.21 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14908.25 | 1515.41 | 1514.21 | 1643.5341 | 153.79 | 129.3241 | 153.79 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 14958.28 | 1513.65 | 1512.45 | 1643.4678 | 155.55 | 131.0178 | 155.55 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15008.28 | 1513.48 | 1512.28 | 1643.4015 | 155.72 | 131.1215 | 155.72 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15058.29 | 1514.47 | 1513.27 | 1643.3352 | 154.73 | 130.0652 | 154.73 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15108.31 | 1515.56 | 1514.36 | 1643.2689 | 153.64 | 128.9089 | 153.64 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15158.31 | 1516.21 | 1515.01 | 1643.2026 | 152.99 | 128.1926 | 152.99 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15208.33 | 1517.7 | 1516.5 | 1643.1363 | 151.5 | 126.6363 | 151.5 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15258.35 | 1518.87 | 1517.67 | 1643.0699 | 150.33 | 125.3999 | 150.33 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15308.35 | 1519.48 | 1518.28 | 1643.0036 | 149.72 | 124.7236 | 149.72 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15358.38 | 1520.88 | 1519.68 | 1642.9373 | 148.32 | 123.2573 | 148.32 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15408.38 | 1520.84 | 1519.64 | 1642.871 | 148.36 | 123.231 | 148.36 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15458.38 | 1521.5 | 1520.3 | 1642.8047 | 147.7 | 122.5047 | 147.7 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15508.44 | 1523.84 | 1522.64 | 1642.7384 | 145.36 | 120.0984 | 145.36 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15558.46 | 1525.15 | 1523.95 | 1642.672 | 144.05 | 118.722 | 144.05 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15608.49 | 1527.14 | 1525.94 | 1642.6057 | 142.06 | 116.6657 | 142.06 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15658.5 | 1527.97 | 1526.77 | 1642.5394 | 141.23 | 115.7694 | 141.23 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15708.54 | 1529.94 | 1528.74 | 1642.4731 | 139.26 | 113.7331 | 139.26 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15758.55 | 1530.98 | 1529.78 | 1642.4068 | 138.22 | 112.6268 | 138.22 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15808.57 | 1532.16 | 1530.96 | 1642.3404 | 137.04 | 111.3804 | 137.04 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15858.58 | 1533.19 | 1531.99 | 1642.2741 | 136.01 | 110.2841 | 136.01 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15908.58 | 1533.96 | 1532.76 | 1642.2078 | 135.24 | 109.4478 | 135.24 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 15958.58 | 1534.41 | 1533.21 | 1642.1415 | 134.79 | 108.9315 | 134.79 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16008.59 | 1535.06 | 1533.86 | 1642.0752 | 134.14 | 108.2152 | 134.14 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16058.59 | 1535.45 | 1534.25 | 1642.0089 | 133.75 | 107.7589 | 133.75 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16108.67 | 1538.34 | 1537.14 | 1641.9426 | 130.86 | 104.8026 | 130.86 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16158.72 | 1540.43 | 1539.23 | 1641.8762 | 128.77 | 102.6462 | 128.77 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16208.78 | 1542.92 | 1541.72 | 1641.8098 | 126.28 | 100.0898 | 126.28 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16258.87 | 1545.92 | 1544.72 | 1641.7434 | 123.28 | 97.0234 | 123.28 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16308.9 | 1547.55 | 1546.35 | 1641.6771 | 121.65 | 95.3271 | 121.65 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16358.96 | 1550.09 | 1548.89 | 1641.6107 | 119.11 | 92.7207 | 119.11 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16408.99 | 1551.83 | 1550.63 | 1641.5444 | 117.37 | 90.9144 | 117.37 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16459.01 | 1553.22 | 1552.02 | 1641.4781 | 115.98 | 89.4581 | 115.98 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16509.04 | 1554.97 | 1553.77 | 1641.4117 | 114.23 | 87.6417 | 114.23 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16559.06 | 1556.26 | 1555.06 | 1641.3454 | 112.94 | 86.2854 | 112.94 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16609.07 | 1557.5 | 1556.3 | 1641.2791 | 111.7 | 84.9791 | 111.7 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16659.07 | 1557.62 | 1556.42 | 1641.2128 | 111.58 | 84.7928 | 111.58 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16709.07 | 1557.46 | 1556.26 | 1641.1465 | 111.74 | 84.8865 | 111.74 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16759.09 | 1556.31 | 1555.11 | 1641.0802 | 112.89 | 85.9702 | 112.89 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16809.07 | 1555.58 | 1554.38 | 1641.0139 | 113.62 | 86.6339 | 113.62 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16859.08 | 1554.69 | 1553.49 | 1640.9476 | 114.51 | 87.4576 | 114.51 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16909.1 | 1553.18 | 1551.98 | 1640.8813 | 116.02 | 88.9013 | 116.02 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 16959.1 | 1553.02 | 1551.82 | 1640.815 | 116.18 | 88.995 | 116.18 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17009.1 | 1552.82 | 1551.62 | 1640.7487 | 116.38 | 89.1287 | 116.38 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17059.1 | 1552.72 | 1551.52 | 1640.6824 | 116.48 | 89.1624 | 116.48 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17109.1 | 1552.64 | 1551.44 | 1640.6161 | 116.56 | 89.1761 | 116.56 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17159.1 | 1552.68 | 1551.48 | 1640.5499 | 116.52 | 89.0699 | 116.52 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17209.1 | 1552.71 | 1551.51 | 1640.4836 | 116.49 | 88.9736 | 116.49 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17259.12 | 1554.1 | 1552.9 | 1640.4172 | 115.1 | 87.5172 | 115.1 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17309.13 | 1554.85 | 1553.65 | 1640.3509 | 114.35 | 86.7009 | 114.35 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17359.13 | 1555.38 | 1554.18 | 1640.2846 | 113.82 | 86.1046 | 113.82 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17409.14 | 1556.56 | 1555.36 | 1640.2183 | 112.64 | 84.8583 | 112.64 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17459.14 | 1556.56 | 1555.36 | 1640.1521 | 112.64 | 84.7921 | 112.64 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17509.15 | 1557.08 | 1555.88 | 1640.0857 | 112.12 | 84.2057 | 112.12 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17559.15 | 1557.54 | 1556.34 | 1640.0195 | 111.66 | 83.6795 | 111.66 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17609.15 | 1558.01 | 1556.81 | 1639.9532 | 111.19 | 83.1432 | 111.19 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17659.15 | 1558.23 | 1557.03 | 1639.8869 | 110.97 | 82.8569 | 110.97 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17709.15 | 1558.01 | 1556.81 | 1639.8206 | 111.19 | 83.0106 | 111.19 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17759.16 | 1557.42 | 1556.22 | 1639.7543 | 111.78 | 83.5343 | 111.78 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17809.16 | 1556.96 | 1555.76 | 1639.688 | 112.24 | 83.928 | 112.24 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17859.16 | 1556.66 | 1555.46 | 1639.6217 | 112.54 | 84.1617 | 112.54 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17909.16 | 1556.64 | 1555.44 | 1639.5554 | 112.56 | 84.1154 | 112.56 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 17959.19 | 1554.8 | 1553.6 | 1639.4891 | 114.4 | 85.8891 | 114.4 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18009.19 | 1554.54 | 1553.34 | 1639.4228 | 114.66 | 86.0828 | 114.66 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18059.2 | 1554.04 | 1552.84 | 1639.3565 | 115.16 | 86.5165 | 115.16 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18109.23 | 1552.27 | 1551.07 | 1639.2901 | 116.93 | 88.2201 | 116.93 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18159.24 | 1553.3 | 1552.1 | 1639.2238 | 115.9 | 87.1238 | 115.9 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18209.4 | 1549.3 | 1548.1 | 1639.1573 | 119.9 | 91.0573 | 119.9 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18259.4 | 1549.47 | 1548.27 | 1639.091 | 119.73 | 90.821 | 119.73 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18309.4 | 1549.49 | 1548.29 | 1639.0247 | 119.71 | 90.7347 | 119.71 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18359.4 | 1549.23 | 1548.03 | 1638.9585 | 119.97 | 90.9285 | 119.97 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18409.4 | 1549.92 | 1548.72 | 1638.8922 | 119.28 | 90.1722 | 119.28 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18459.43 | 1551.45 | 1550.25 | 1638.8258 | 117.75 | 88.5758 | 117.75 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18509.53 | 1554.68 | 1553.48 | 1638.7594 | 114.52 | 85.2794 | 114.52 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18559.53 | 1555.31 | 1554.11 | 1638.6931 | 113.89 | 84.5831 | 113.89 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18608.66 | 1556.12 | 1554.92 | 1638.628 | 113.08 | 83.708 | 113.08 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18658.69 | 1557.85 | 1556.65 | 1638.5616 | 111.35 | 81.9116 | 111.35 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18708.7 | 1558.72 | 1557.52 | 1638.4953 | 110.48 | 80.9753 | 110.48 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18758.71 | 1559.56 | 1558.36 | 1638.429 | 109.64 | 80.069 | 109.64 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18808.73 | 1560.98 | 1559.78 | 1638.3627 | 108.22 | 78.5827 | 108.22 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18858.73 | 1561.8 | 1560.6 | 1638.2964 | 107.4 | 77.6964 | 107.4 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18908.74 | 1562.31 | 1561.11 | 1638.2301 | 106.89 | 77.1201 | 106.89 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 18958.74 | 1563.01 | 1561.81 | 1638.1638 | 106.19 | 76.3538 | 106.19 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19008.76 | 1564.44 | 1563.24 | 1638.0975 | 104.76 | 74.8575 | 104.76 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19058.77 | 1565.23 | 1564.03 | 1638.0312 | 103.97 | 74.0012 | 103.97 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19108.77 | 1565.42 | 1564.22 | 1637.9649 | 103.78 | 73.7449 | 103.78 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19158.78 | 1566.4 | 1565.2 | 1637.8986 | 102.8 | 72.6986 | 102.8 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19208.78 | 1566.96 | 1565.76 | 1637.8323 | 102.24 | 72.0723 | 102.24 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19258.79 | 1567.73 | 1566.53 | 1637.766 | 101.47 | 71.236 | 101.47 | PN10 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19308.79 | 1568 | 1566.8 | 1637.6997 | 101.2 | 70.8997 | 101.2 | PN10 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19358.79 | 1568.73 | 1567.53 | 1637.6334 | 100.47 | 70.1034 | 100.47 | PN10 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19408.79 | 1568.84 | 1567.64 | 1637.5671 | 100.36 | 69.9271 | 100.36 | PN10 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19458.79 | 1568.92 | 1567.72 | 1637.5008 | 100.28 | 69.7808 | 100.28 | PN10 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19508.79 | 1568.78 | 1567.58 | 1637.4346 | 100.42 | 69.8546 | 100.42 | PN10 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19558.79 | 1568.78 | 1567.58 | 1637.3683 | 100.42 | 69.7883 | 100.42 | PN10 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19608.79 | 1568.33 | 1567.13 | 1637.302 | 100.87 | 70.172 | 100.87 | PN10 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19658.79 | 1568.25 | 1567.05 | 1637.2357 | 100.95 | 70.1857 | 100.95 | PN10 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19708.81 | 1567.07 | 1565.87 | 1637.1694 | 102.13 | 71.2994 | 102.13 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19758.82 | 1565.85 | 1564.65 | 1637.1031 | 103.35 | 72.4531 | 103.35 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19808.82 | 1565.86 | 1564.66 | 1637.0368 | 103.34 | 72.3768 | 103.34 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19858.84 | 1564.67 | 1563.47 | 1636.9704 | 104.53 | 73.5004 | 104.53 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19908.84 | 1563.87 | 1562.67 | 1636.9042 | 105.33 | 74.2342 | 105.33 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 19958.84 | 1564 | 1562.8 | 1636.8379 | 105.2 | 74.0379 | 105.2 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20008.85 | 1563.5 | 1562.3 | 1636.7716 | 105.7 | 74.4716 | 105.7 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20058.86 | 1562.31 | 1561.11 | 1636.7052 | 106.89 | 75.5952 | 106.89 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20108.86 | 1562.24 | 1561.04 | 1636.639 | 106.96 | 75.599 | 106.96 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20158.86 | 1561.91 | 1560.71 | 1636.5727 | 107.29 | 75.8627 | 107.29 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20208.86 | 1561.64 | 1560.44 | 1636.5064 | 107.56 | 76.0664 | 107.56 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20258.86 | 1561.91 | 1560.71 | 1636.4401 | 107.29 | 75.7301 | 107.29 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20308.89 | 1560.26 | 1559.06 | 1636.3737 | 108.94 | 77.3137 | 108.94 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20358.9 | 1559.37 | 1558.17 | 1636.3074 | 109.83 | 78.1374 | 109.83 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20408.91 | 1558.16 | 1556.96 | 1636.2411 | 111.04 | 79.2811 | 111.04 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20458.91 | 1558.02 | 1556.82 | 1636.1748 | 111.18 | 79.3548 | 111.18 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20508.94 | 1556.35 | 1555.15 | 1636.1085 | 112.85 | 80.9585 | 112.85 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20559.02 | 1553.59 | 1552.39 | 1636.0421 | 115.61 | 83.6521 | 115.61 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20609.02 | 1553.42 | 1552.22 | 1635.9758 | 115.78 | 83.7558 | 115.78 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20659.04 | 1551.78 | 1550.58 | 1635.9095 | 117.42 | 85.3295 | 117.42 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20709.05 | 1551.36 | 1550.16 | 1635.8432 | 117.84 | 85.6832 | 117.84 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20759.25 | 1546.8 | 1545.6 | 1635.7766 | 122.4 | 90.1766 | 122.4 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20809.25 | 1546.52 | 1545.32 | 1635.7104 | 122.68 | 90.3904 | 122.68 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20859.34 | 1543.58 | 1542.38 | 1635.6439 | 125.62 | 93.2639 | 125.62 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20909.43 | 1540.56 | 1539.36 | 1635.5775 | 128.64 | 96.2175 | 128.64 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 20959.48 | 1538.39 | 1537.19 | 1635.5112 | 130.81 | 98.3212 | 130.81 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21009.51 | 1536.67 | 1535.47 | 1635.4448 | 132.53 | 99.9748 | 132.53 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21059.57 | 1534.2 | 1533 | 1635.3785 | 135 | 102.3785 | 135 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21109.65 | 1531.33 | 1530.13 | 1635.3121 | 137.87 | 105.1821 | 137.87 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21159.68 | 1529.77 | 1528.57 | 1635.2457 | 139.43 | 106.6757 | 139.43 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21209.78 | 1526.49 | 1525.29 | 1635.1793 | 142.71 | 109.8893 | 142.71 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21259.82 | 1524.57 | 1523.37 | 1635.113 | 144.63 | 111.743 | 144.63 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21309.88 | 1522.14 | 1520.94 | 1635.0466 | 147.06 | 114.1066 | 147.06 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21359.93 | 1519.98 | 1518.78 | 1634.9802 | 149.22 | 116.2002 | 149.22 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21409.97 | 1517.9 | 1516.7 | 1634.9139 | 151.3 | 118.2139 | 151.3 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21460.03 | 1515.48 | 1514.28 | 1634.8475 | 153.72 | 120.5675 | 153.72 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21510.05 | 1513.9 | 1512.7 | 1634.7812 | 155.3 | 122.0812 | 155.3 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21560.09 | 1511.94 | 1510.74 | 1634.7149 | 157.26 | 123.9749 | 157.26 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21610.22 | 1508.31 | 1507.11 | 1634.6484 | 160.89 | 127.5384 | 160.89 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21660.23 | 1509.38 | 1508.18 | 1634.5821 | 159.82 | 126.4021 | 159.82 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21710.25 | 1510.71 | 1509.51 | 1634.5158 | 158.49 | 125.0058 | 158.49 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21760.26 | 1511.38 | 1510.18 | 1634.4495 | 157.82 | 124.2695 | 157.82 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21810.32 | 1513.92 | 1512.72 | 1634.3831 | 155.28 | 121.6631 | 155.28 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21860.33 | 1514.86 | 1513.66 | 1634.3168 | 154.34 | 120.6568 | 154.34 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21910.39 | 1517.41 | 1516.21 | 1634.2504 | 151.79 | 118.0404 | 151.79 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 21960.42 | 1518.85 | 1517.65 | 1634.1841 | 150.35 | 116.5341 | 150.35 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22010.44 | 1520.5 | 1519.3 | 1634.1178 | 148.7 | 114.8178 | 148.7 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22060.48 | 1522.32 | 1521.12 | 1634.0514 | 146.88 | 112.9314 | 146.88 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22110.49 | 1523.61 | 1522.41 | 1633.9851 | 145.59 | 111.5751 | 145.59 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22160.5 | 1524.48 | 1523.28 | 1633.9188 | 144.72 | 110.6388 | 144.72 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22210.52 | 1525.8 | 1524.6 | 1633.8525 | 143.4 | 109.2525 | 143.4 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22260.53 | 1526.68 | 1525.48 | 1633.7862 | 142.52 | 108.3062 | 142.52 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22310.54 | 1528.09 | 1526.89 | 1633.7199 | 141.11 | 106.8299 | 141.11 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22360.56 | 1529.29 | 1528.09 | 1633.6536 | 139.91 | 105.5636 | 139.91 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22410.56 | 1529.85 | 1528.65 | 1633.5873 | 139.35 | 104.9373 | 139.35 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22460.57 | 1530.56 | 1529.36 | 1633.521 | 138.64 | 104.161 | 138.64 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22510.58 | 1531.47 | 1530.27 | 1633.4547 | 137.73 | 103.1847 | 137.73 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22560.58 | 1531.68 | 1530.48 | 1633.3884 | 137.52 | 102.9084 | 137.52 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22610.58 | 1532.05 | 1530.85 | 1633.3221 | 137.15 | 102.4721 | 137.15 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22660.58 | 1532.43 | 1531.23 | 1633.2558 | 136.77 | 102.0258 | 136.77 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22710.58 | 1532.69 | 1531.49 | 1633.1895 | 136.51 | 101.6995 | 136.51 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22760.58 | 1532.13 | 1530.93 | 1633.1232 | 137.07 | 102.1932 | 137.07 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22810.58 | 1532.23 | 1531.03 | 1633.0569 | 136.97 | 102.0269 | 136.97 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22860.58 | 1531.91 | 1530.71 | 1632.9906 | 137.29 | 102.2806 | 137.29 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22910.58 | 1531.9 | 1530.7 | 1632.9243 | 137.3 | 102.2243 | 137.3 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 22960.58 | 1531.62 | 1530.42 | 1632.858 | 137.58 | 102.438 | 137.58 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23010.59 | 1531.32 | 1530.12 | 1632.7917 | 137.88 | 102.6717 | 137.88 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23060.59 | 1531.19 | 1529.99 | 1632.7254 | 138.01 | 102.7354 | 138.01 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23110.59 | 1530.74 | 1529.54 | 1632.6592 | 138.46 | 103.1192 | 138.46 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23160.59 | 1530.46 | 1529.26 | 1632.5929 | 138.74 | 103.3329 | 138.74 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23210.59 | 1530.06 | 1528.86 | 1632.5266 | 139.14 | 103.6666 | 139.14 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23260.61 | 1528.78 | 1527.58 | 1632.4603 | 140.42 | 104.8803 | 140.42 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23310.61 | 1527.93 | 1526.73 | 1632.394 | 141.27 | 105.664 | 141.27 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23360.62 | 1527.06 | 1525.86 | 1632.3277 | 142.14 | 106.4677 | 142.14 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23410.65 | 1525.43 | 1524.23 | 1632.2613 | 143.77 | 108.0313 | 143.77 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23460.66 | 1524.13 | 1522.93 | 1632.195 | 145.07 | 109.265 | 145.07 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23510.68 | 1522.99 | 1521.79 | 1632.1287 | 146.21 | 110.3387 | 146.21 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23560.74 | 1520.49 | 1519.29 | 1632.0623 | 148.71 | 112.7723 | 148.71 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23610.76 | 1519.11 | 1517.91 | 1631.996 | 150.09 | 114.086 | 150.09 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23660.79 | 1517.38 | 1516.18 | 1631.9297 | 151.82 | 115.7497 | 151.82 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23710.81 | 1515.88 | 1514.68 | 1631.8634 | 153.32 | 117.1834 | 153.32 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23760.84 | 1514.2 | 1513 | 1631.797 | 155 | 118.797 | 155 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23810.86 | 1512.64 | 1511.44 | 1631.7307 | 156.56 | 120.2907 | 156.56 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23860.86 | 1512.59 | 1511.39 | 1631.6644 | 156.61 | 120.2744 | 156.61 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23910.91 | 1510.42 | 1509.22 | 1631.5981 | 158.78 | 122.3781 | 158.78 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 23960.94 | 1508.83 | 1507.63 | 1631.5317 | 160.37 | 123.9017 | 160.37 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24010.96 | 1507.23 | 1506.03 | 1631.4654 | 161.97 | 125.4354 | 161.97 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24060.97 | 1506.12 | 1504.92 | 1631.3991 | 163.08 | 126.4791 | 163.08 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24111.01 | 1504.19 | 1502.99 | 1631.3328 | 165.01 | 128.3428 | 165.01 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24161.04 | 1502.53 | 1501.33 | 1631.2664 | 166.67 | 129.9364 | 166.67 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24211.07 | 1500.76 | 1499.56 | 1631.2001 | 168.44 | 131.6401 | 168.44 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24261.1 | 1499.18 | 1497.98 | 1631.1338 | 170.02 | 133.1538 | 170.02 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24311.1 | 1499.28 | 1498.08 | 1631.0675 | 169.92 | 132.9875 | 169.92 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24361.1 | 1499.08 | 1497.88 | 1631.0012 | 170.12 | 133.1212 | 170.12 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24411.11 | 1500.1 | 1498.9 | 1630.9349 | 169.1 | 132.0349 | 169.1 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24461.13 | 1501.73 | 1500.53 | 1630.8686 | 167.47 | 130.3386 | 167.47 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24511.18 | 1503.97 | 1502.77 | 1630.8022 | 165.23 | 128.0322 | 165.23 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24561.21 | 1505.55 | 1504.35 | 1630.7359 | 163.65 | 126.3859 | 163.65 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24611.25 | 1507.56 | 1506.36 | 1630.6695 | 161.64 | 124.3095 | 161.64 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24661.28 | 1509.2 | 1508 | 1630.6032 | 160 | 122.6032 | 160 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24711.31 | 1511.11 | 1509.91 | 1630.5369 | 158.09 | 120.6269 | 158.09 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24761.32 | 1511.99 | 1510.79 | 1630.4706 | 157.21 | 119.6806 | 157.21 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24811.35 | 1513.61 | 1512.41 | 1630.4042 | 155.59 | 117.9942 | 155.59 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24861.35 | 1514.24 | 1513.04 | 1630.3379 | 154.96 | 117.2979 | 154.96 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24911.35 | 1514.9 | 1513.7 | 1630.2716 | 154.3 | 116.5716 | 154.3 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 24961.36 | 1515.55 | 1514.35 | 1630.2053 | 153.65 | 115.8553 | 153.65 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25011.36 | 1515.78 | 1514.58 | 1630.139 | 153.42 | 115.559 | 153.42 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25061.36 | 1515.32 | 1514.12 | 1630.0728 | 153.88 | 115.9528 | 153.88 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25111.36 | 1515.42 | 1514.22 | 1630.0065 | 153.78 | 115.7865 | 153.78 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25161.36 | 1514.89 | 1513.69 | 1629.9402 | 154.31 | 116.2502 | 154.31 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25211.37 | 1515.52 | 1514.32 | 1629.8739 | 153.68 | 115.5539 | 153.68 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25261.37 | 1514.85 | 1513.65 | 1629.8076 | 154.35 | 116.1576 | 154.35 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25311.37 | 1514.4 | 1513.2 | 1629.7413 | 154.8 | 116.5413 | 154.8 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25361.38 | 1513.87 | 1512.67 | 1629.675 | 155.33 | 117.005 | 155.33 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25411.39 | 1512.97 | 1511.77 | 1629.6087 | 156.23 | 117.8387 | 156.23 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25461.39 | 1512.08 | 1510.88 | 1629.5424 | 157.12 | 118.6624 | 157.12 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25511.42 | 1510.47 | 1509.27 | 1629.4761 | 158.73 | 120.2061 | 158.73 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25561.44 | 1509 | 1507.8 | 1629.4097 | 160.2 | 121.6097 | 160.2 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25611.45 | 1507.92 | 1506.72 | 1629.3434 | 161.28 | 122.6234 | 161.28 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25661.53 | 1505.22 | 1504.02 | 1629.277 | 163.98 | 125.257 | 163.98 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25711.56 | 1503.5 | 1502.3 | 1629.2107 | 165.7 | 126.9107 | 165.7 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25761.59 | 1501.62 | 1500.42 | 1629.1444 | 167.58 | 128.7244 | 167.58 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25811.64 | 1499.46 | 1498.26 | 1629.078 | 169.74 | 130.818 | 169.74 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25861.73 | 1496.4 | 1495.2 | 1629.0116 | 172.8 | 133.8116 | 172.8 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25911.77 | 1494.46 | 1493.26 | 1628.9453 | 174.74 | 135.6853 | 174.74 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 25961.86 | 1491.45 | 1490.25 | 1628.8788 | 177.75 | 138.6288 | 177.75 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26011.99 | 1487.84 | 1486.64 | 1628.8124 | 181.36 | 142.1724 | 181.36 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26062.21 | 1483.08 | 1481.88 | 1628.7458 | 186.12 | 146.8658 | 186.12 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26112.37 | 1479.18 | 1477.98 | 1628.6793 | 190.02 | 150.6993 | 190.02 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26162.37 | 1479.48 | 1478.28 | 1628.613 | 189.72 | 150.333 | 189.72 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26212.77 | 1485.85 | 1484.65 | 1628.5462 | 183.35 | 143.8962 | 183.35 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26262.88 | 1489.21 | 1488.01 | 1628.4797 | 179.99 | 140.4697 | 179.99 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26312.2 | 1491.1 | 1489.9 | 1628.4143 | 178.1 | 138.5143 | 178.1 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26362.23 | 1492.86 | 1491.66 | 1628.348 | 176.34 | 136.688 | 176.34 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26412.26 | 1494.57 | 1493.37 | 1628.2817 | 174.63 | 134.9117 | 174.63 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26462.28 | 1495.9 | 1494.7 | 1628.2154 | 173.3 | 133.5154 | 173.3 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26512.3 | 1497.18 | 1495.98 | 1628.149 | 172.02 | 132.169 | 172.02 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26562.3 | 1497.99 | 1496.79 | 1628.0828 | 171.21 | 131.2928 | 171.21 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26612.31 | 1498.67 | 1497.47 | 1628.0165 | 170.53 | 130.5465 | 170.53 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26662.31 | 1498.24 | 1497.04 | 1627.9502 | 170.96 | 130.9102 | 170.96 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26712.31 | 1497.87 | 1496.67 | 1627.8839 | 171.33 | 131.2139 | 171.33 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26762.35 | 1495.81 | 1494.61 | 1627.8175 | 173.39 | 133.2075 | 173.39 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26812.35 | 1495.3 | 1494.1 | 1627.7512 | 173.9 | 133.6512 | 173.9 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26862.37 | 1494.03 | 1492.83 | 1627.6849 | 175.17 | 134.8549 | 175.17 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26912.4 | 1492.19 | 1490.99 | 1627.6186 | 177.01 | 136.6286 | 177.01 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 26962.43 | 1490.65 | 1489.45 | 1627.5522 | 178.55 | 138.1022 | 178.55 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27012.46 | 1488.98 | 1487.78 | 1627.4859 | 180.22 | 139.7059 | 180.22 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27062.51 | 1486.62 | 1485.42 | 1627.4196 | 182.58 | 141.9996 | 182.58 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27112.54 | 1484.97 | 1483.77 | 1627.3532 | 184.23 | 143.5832 | 184.23 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27162.58 | 1482.9 | 1481.7 | 1627.2869 | 186.3 | 145.5869 | 186.3 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27212.6 | 1481.6 | 1480.4 | 1627.2206 | 187.6 | 146.8206 | 187.6 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27262.61 | 1482.43 | 1481.23 | 1627.1543 | 186.77 | 145.9243 | 186.77 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27312.62 | 1483.56 | 1482.36 | 1627.088 | 185.64 | 144.728 | 185.64 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27362.65 | 1485.3 | 1484.1 | 1627.0216 | 183.9 | 142.9216 | 183.9 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27412.66 | 1486.32 | 1485.12 | 1626.9553 | 182.88 | 141.8353 | 182.88 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27462.66 | 1487.08 | 1485.88 | 1626.889 | 182.12 | 141.009 | 182.12 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27512.66 | 1486.97 | 1485.77 | 1626.8227 | 182.23 | 141.0527 | 182.23 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27562.67 | 1487.35 | 1486.15 | 1626.7564 | 181.85 | 140.6064 | 181.85 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27612.67 | 1487.56 | 1486.36 | 1626.6901 | 181.64 | 140.3301 | 181.64 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27662.68 | 1486.22 | 1485.02 | 1626.6238 | 182.98 | 141.6038 | 182.98 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27712.69 | 1485.93 | 1484.73 | 1626.5575 | 183.27 | 141.8275 | 183.27 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27762.71 | 1484.33 | 1483.13 | 1626.4912 | 184.87 | 143.3612 | 184.87 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27812.75 | 1482.39 | 1481.19 | 1626.4249 | 186.81 | 145.2349 | 186.81 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27862.76 | 1481.31 | 1480.11 | 1626.3586 | 187.89 | 146.2486 | 187.89 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27912.82 | 1478.91 | 1477.71 | 1626.2922 | 190.29 | 148.5822 | 190.29 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 27962.86 | 1476.8 | 1475.6 | 1626.2258 | 192.4 | 150.6258 | 192.4 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28012.91 | 1474.64 | 1473.44 | 1626.1595 | 194.56 | 152.7195 | 194.56 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28062.92 | 1475.41 | 1474.21 | 1626.0932 | 193.79 | 151.8832 | 193.79 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28112.95 | 1477.38 | 1476.18 | 1626.0268 | 191.82 | 149.8468 | 191.82 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28162.98 | 1478.85 | 1477.65 | 1625.9605 | 190.35 | 148.3105 | 190.35 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28213.02 | 1480.95 | 1479.75 | 1625.8942 | 188.25 | 146.1442 | 188.25 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28263.08 | 1483.44 | 1482.24 | 1625.8278 | 185.76 | 143.5878 | 185.76 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28313.09 | 1484.11 | 1482.91 | 1625.7615 | 185.09 | 142.8515 | 185.09 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28363.16 | 1486.81 | 1485.61 | 1625.6951 | 182.39 | 140.0851 | 182.39 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28413.17 | 1488.06 | 1486.86 | 1625.6288 | 181.14 | 138.7688 | 181.14 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28463.18 | 1488.62 | 1487.42 | 1625.5625 | 180.58 | 138.1425 | 180.58 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28513.18 | 1489.09 | 1487.89 | 1625.4962 | 180.11 | 137.6062 | 180.11 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28563.18 | 1489.62 | 1488.42 | 1625.4299 | 179.58 | 137.0099 | 179.58 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28613.18 | 1489.62 | 1488.42 | 1625.3636 | 179.58 | 136.9436 | 179.58 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28663.2 | 1490.74 | 1489.54 | 1625.2973 | 178.46 | 135.7573 | 178.46 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28713.2 | 1490.81 | 1489.61 | 1625.231 | 178.39 | 135.621 | 178.39 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28763.2 | 1490.19 | 1488.99 | 1625.1647 | 179.01 | 136.1747 | 179.01 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28813.2 | 1491.38 | 1490.18 | 1625.0984 | 177.82 | 134.9184 | 177.82 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28863.21 | 1490.52 | 1489.32 | 1625.0321 | 178.68 | 135.7121 | 178.68 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28913.21 | 1489.88 | 1488.68 | 1624.9658 | 179.32 | 136.2858 | 179.32 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 28963.22 | 1488.96 | 1487.76 | 1624.8995 | 180.24 | 137.1395 | 180.24 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29013.24 | 1487.71 | 1486.51 | 1624.8332 | 181.49 | 138.3232 | 181.49 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29063.24 | 1486.96 | 1485.76 | 1624.7669 | 182.24 | 139.0069 | 182.24 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29113.26 | 1485.9 | 1484.7 | 1624.7006 | 183.3 | 140.0006 | 183.3 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29163.32 | 1483.27 | 1482.07 | 1624.6342 | 185.93 | 142.5642 | 185.93 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29213.33 | 1483.63 | 1482.43 | 1624.5679 | 185.57 | 142.1379 | 185.57 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29263.34 | 1482.36 | 1481.16 | 1624.5016 | 186.84 | 143.3416 | 186.84 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29313.34 | 1482.26 | 1481.06 | 1624.4353 | 186.94 | 143.3753 | 186.94 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29363.36 | 1483.68 | 1482.48 | 1624.369 | 185.52 | 141.889 | 185.52 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29413.37 | 1484.59 | 1483.39 | 1624.3027 | 184.61 | 140.9127 | 184.61 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29463.39 | 1485.79 | 1484.59 | 1624.2364 | 183.41 | 139.6464 | 183.41 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29513.39 | 1486.52 | 1485.32 | 1624.1701 | 182.68 | 138.8501 | 182.68 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29563.39 | 1487 | 1485.8 | 1624.1038 | 182.2 | 138.3038 | 182.2 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29613.39 | 1487.45 | 1486.25 | 1624.0375 | 181.75 | 137.7875 | 181.75 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29663.4 | 1487.2 | 1486 | 1623.9712 | 182 | 137.9712 | 182 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29713.4 | 1486.51 | 1485.31 | 1623.9049 | 182.69 | 138.5949 | 182.69 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29763.4 | 1485.88 | 1484.68 | 1623.8386 | 183.32 | 139.1586 | 183.32 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29813.41 | 1486.33 | 1485.13 | 1623.7723 | 182.87 | 138.6423 | 182.87 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29863.41 | 1486.23 | 1485.03 | 1623.706 | 182.97 | 138.676 | 182.97 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29913.41 | 1485.79 | 1484.59 | 1623.6397 | 183.41 | 139.0497 | 183.41 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 29963.42 | 1486.74 | 1485.54 | 1623.5734 | 182.46 | 138.0334 | 182.46 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30013.42 | 1486.73 | 1485.53 | 1623.5071 | 182.47 | 137.9771 | 182.47 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30063.42 | 1487.13 | 1485.93 | 1623.4408 | 182.07 | 137.5108 | 182.07 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30113.42 | 1487.36 | 1486.16 | 1623.3746 | 181.84 | 137.2146 | 181.84 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30163.42 | 1486.61 | 1485.41 | 1623.3083 | 182.59 | 137.8983 | 182.59 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30213.43 | 1486.52 | 1485.32 | 1623.242 | 182.68 | 137.922 | 182.68 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30263.43 | 1486.24 | 1485.04 | 1623.1757 | 182.96 | 138.1357 | 182.96 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30313.43 | 1485.34 | 1484.14 | 1623.1094 | 183.86 | 138.9694 | 183.86 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30363.45 | 1483.94 | 1482.74 | 1623.0431 | 185.26 | 140.3031 | 185.26 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30413.28 | 1483.19 | 1481.99 | 1622.977 | 186.01 | 140.987 | 186.01 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30463.28 | 1483.01 | 1481.81 | 1622.9107 | 186.19 | 141.1007 | 186.19 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30513.32 | 1481.06 | 1479.86 | 1622.8444 | 188.14 | 142.9844 | 188.14 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30563.35 | 1479.18 | 1477.98 | 1622.778 | 190.02 | 144.798 | 190.02 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30613.38 | 1477.61 | 1476.41 | 1622.7117 | 191.59 | 146.3017 | 191.59 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30663.42 | 1475.47 | 1474.27 | 1622.6453 | 193.73 | 148.3753 | 193.73 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30713.49 | 1472.9 | 1471.7 | 1622.579 | 196.3 | 150.879 | 196.3 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30763.56 | 1470.31 | 1469.11 | 1622.5126 | 198.89 | 153.4026 | 198.89 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30813.58 | 1468.81 | 1467.61 | 1622.4463 | 200.39 | 154.8363 | 200.39 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30863.67 | 1465.72 | 1464.52 | 1622.3798 | 203.48 | 157.8598 | 203.48 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30913.75 | 1462.91 | 1461.71 | 1622.3134 | 206.29 | 160.6034 | 206.29 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 30963.94 | 1458.62 | 1457.42 | 1622.2469 | 210.58 | 164.8269 | 210.58 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31014.01 | 1455.93 | 1454.73 | 1622.1805 | 213.27 | 167.4505 | 213.27 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31064.27 | 1450.82 | 1449.62 | 1622.1139 | 218.38 | 172.4939 | 218.38 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31114.29 | 1452.27 | 1451.07 | 1622.0476 | 216.93 | 170.9776 | 216.93 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31164.44 | 1456.1 | 1454.9 | 1621.9811 | 213.1 | 167.0811 | 213.1 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31214.49 | 1458.46 | 1457.26 | 1621.9147 | 210.74 | 164.6547 | 210.74 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31264.56 | 1461.02 | 1459.82 | 1621.8483 | 208.18 | 162.0283 | 208.18 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31314.74 | 1465.32 | 1464.12 | 1621.7818 | 203.88 | 157.6618 | 203.88 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31364.89 | 1469.15 | 1467.95 | 1621.7153 | 200.05 | 153.7653 | 200.05 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31415.03 | 1472.97 | 1471.77 | 1621.6488 | 196.23 | 149.8788 | 196.23 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31465.2 | 1477 | 1475.8 | 1621.5823 | 192.2 | 145.7823 | 192.2 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31515.32 | 1480.56 | 1479.36 | 1621.5159 | 188.64 | 142.1559 | 188.64 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31565.38 | 1482.91 | 1481.71 | 1621.4495 | 186.29 | 139.7395 | 186.29 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31615.49 | 1486.2 | 1485 | 1621.3831 | 183 | 136.3831 | 183 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31665.6 | 1489.61 | 1488.41 | 1621.3166 | 179.59 | 132.9066 | 179.59 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31715.6 | 1489.75 | 1488.55 | 1621.2503 | 179.45 | 132.7003 | 179.45 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31765.64 | 1491.74 | 1490.54 | 1621.184 | 177.46 | 130.644 | 177.46 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31815.68 | 1493.77 | 1492.57 | 1621.1176 | 175.43 | 128.5476 | 175.43 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31865.73 | 1495.98 | 1494.78 | 1621.0513 | 173.22 | 126.2713 | 173.22 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31915.73 | 1496.14 | 1494.94 | 1620.985 | 173.06 | 126.045 | 173.06 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 31965.75 | 1497.38 | 1496.18 | 1620.9187 | 171.82 | 124.7387 | 171.82 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32015.75 | 1497.77 | 1496.57 | 1620.8524 | 171.43 | 124.2824 | 171.43 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32065.75 | 1497.57 | 1496.37 | 1620.7861 | 171.63 | 124.4161 | 171.63 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32115.75 | 1497.64 | 1496.44 | 1620.7198 | 171.56 | 124.2798 | 171.56 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32165.76 | 1496.59 | 1495.39 | 1620.6535 | 172.61 | 125.2635 | 172.61 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32215.78 | 1495.34 | 1494.14 | 1620.5872 | 173.86 | 126.4472 | 173.86 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32265.78 | 1495.24 | 1494.04 | 1620.5209 | 173.96 | 126.4809 | 173.96 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32315.79 | 1494.08 | 1492.88 | 1620.4546 | 175.12 | 127.5746 | 175.12 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32365.79 | 1493.81 | 1492.61 | 1620.3883 | 175.39 | 127.7783 | 175.39 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32415.82 | 1492.1 | 1490.9 | 1620.322 | 177.1 | 129.422 | 177.1 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32465.85 | 1490.33 | 1489.13 | 1620.2556 | 178.87 | 131.1256 | 178.87 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32515.86 | 1489.75 | 1488.55 | 1620.1893 | 179.45 | 131.6393 | 179.45 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32565.86 | 1489.07 | 1487.87 | 1620.123 | 180.13 | 132.253 | 180.13 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32615.86 | 1489.66 | 1488.46 | 1620.0567 | 179.54 | 131.5967 | 179.54 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32665.87 | 1488.8 | 1487.6 | 1619.9904 | 180.4 | 132.3904 | 180.4 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32715.87 | 1488.17 | 1486.97 | 1619.9241 | 181.03 | 132.9541 | 181.03 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32765.9 | 1486.56 | 1485.36 | 1619.8578 | 182.64 | 134.4978 | 182.64 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32815.91 | 1485.65 | 1484.45 | 1619.7915 | 183.55 | 135.3415 | 183.55 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32865.92 | 1484.73 | 1483.53 | 1619.7252 | 184.47 | 136.1952 | 184.47 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32915.92 | 1484.82 | 1483.62 | 1619.6589 | 184.38 | 136.0389 | 184.38 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 32965.94 | 1483.45 | 1482.25 | 1619.5926 | 185.75 | 137.3426 | 185.75 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33015.98 | 1481.37 | 1480.17 | 1619.5262 | 187.83 | 139.3562 | 187.83 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33065.99 | 1482.36 | 1481.16 | 1619.4599 | 186.84 | 138.2999 | 186.84 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33116.01 | 1480.82 | 1479.62 | 1619.3936 | 188.38 | 139.7736 | 188.38 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33166.02 | 1480.38 | 1479.18 | 1619.3273 | 188.82 | 140.1473 | 188.82 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33216.02 | 1480.15 | 1478.95 | 1619.261 | 189.05 | 140.311 | 189.05 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33266.02 | 1479.62 | 1478.42 | 1619.1947 | 189.58 | 140.7747 | 189.58 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33316.02 | 1479.34 | 1478.14 | 1619.1284 | 189.86 | 140.9884 | 189.86 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33366.03 | 1478.27 | 1477.07 | 1619.0621 | 190.93 | 141.9921 | 190.93 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33416.03 | 1478.69 | 1477.49 | 1618.9958 | 190.51 | 141.5058 | 190.51 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33466.03 | 1479.11 | 1477.91 | 1618.9295 | 190.09 | 141.0195 | 190.09 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33516.05 | 1477.93 | 1476.73 | 1618.8632 | 191.27 | 142.1332 | 191.27 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33566.09 | 1479.91 | 1478.71 | 1618.7969 | 189.29 | 140.0869 | 189.29 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33616.16 | 1482.62 | 1481.42 | 1618.7305 | 186.58 | 137.3105 | 186.58 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33666.19 | 1484.3 | 1483.1 | 1618.6642 | 184.9 | 135.5642 | 184.9 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33716.31 | 1487.82 | 1486.62 | 1618.5977 | 181.38 | 131.9777 | 181.38 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33766.32 | 1488.67 | 1487.47 | 1618.5314 | 180.53 | 131.0614 | 180.53 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33816.41 | 1491.61 | 1490.41 | 1618.465 | 177.59 | 128.055 | 177.59 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33866.5 | 1494.7 | 1493.5 | 1618.3986 | 174.5 | 124.8986 | 174.5 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33916.51 | 1495.41 | 1494.21 | 1618.3323 | 173.79 | 124.1223 | 173.79 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 33966.54 | 1497.31 | 1496.11 | 1618.266 | 171.89 | 122.156 | 171.89 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34016.56 | 1498.6 | 1497.4 | 1618.1996 | 170.6 | 120.7996 | 170.6 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34066.58 | 1500.12 | 1498.92 | 1618.1333 | 169.08 | 119.2133 | 169.08 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34116.59 | 1500.97 | 1499.77 | 1618.067 | 168.23 | 118.297 | 168.23 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34166.59 | 1501.46 | 1500.26 | 1618.0007 | 167.74 | 117.7407 | 167.74 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34216.6 | 1502.59 | 1501.39 | 1617.9344 | 166.61 | 116.5444 | 166.61 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34266.61 | 1503.02 | 1501.82 | 1617.8681 | 166.18 | 116.0481 | 166.18 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34316.61 | 1503.11 | 1501.91 | 1617.8018 | 166.09 | 115.8918 | 166.09 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34366.61 | 1503.19 | 1501.99 | 1617.7355 | 166.01 | 115.7455 | 166.01 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34416.61 | 1503.98 | 1502.78 | 1617.6692 | 165.22 | 114.8892 | 165.22 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34466.61 | 1503.65 | 1502.45 | 1617.6029 | 165.55 | 115.1529 | 165.55 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34516.62 | 1504.63 | 1503.43 | 1617.5366 | 164.57 | 114.1066 | 164.57 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34566.64 | 1505.99 | 1504.79 | 1617.4703 | 163.21 | 112.6803 | 163.21 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34616.64 | 1505.77 | 1504.57 | 1617.404 | 163.43 | 112.834 | 163.43 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34666.67 | 1507.35 | 1506.15 | 1617.3377 | 161.85 | 111.1877 | 161.85 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34716.69 | 1508.8 | 1507.6 | 1617.2714 | 160.4 | 109.6714 | 160.4 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34766.69 | 1508.57 | 1507.37 | 1617.2051 | 160.63 | 109.8351 | 160.63 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34816.7 | 1509.71 | 1508.51 | 1617.1388 | 159.49 | 108.6288 | 159.49 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34866.7 | 1510.22 | 1509.02 | 1617.0725 | 158.98 | 108.0525 | 158.98 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34916.71 | 1510.63 | 1509.43 | 1617.0062 | 158.57 | 107.5762 | 158.57 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 34966.71 | 1510.39 | 1509.19 | 1616.9399 | 158.81 | 107.7499 | 158.81 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35016.71 | 1510.05 | 1508.85 | 1616.8736 | 159.15 | 108.0236 | 159.15 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35066.72 | 1509.19 | 1507.99 | 1616.8073 | 160.01 | 108.8173 | 160.01 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35116.72 | 1508.8 | 1507.6 | 1616.741 | 160.4 | 109.141 | 160.4 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35166.73 | 1507.84 | 1506.64 | 1616.6747 | 161.36 | 110.0347 | 161.36 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35216.74 | 1506.86 | 1505.66 | 1616.6084 | 162.34 | 110.9484 | 162.34 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35266.75 | 1505.84 | 1504.64 | 1616.5421 | 163.36 | 111.9021 | 163.36 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35316.75 | 1505.65 | 1504.45 | 1616.4758 | 163.55 | 112.0258 | 163.55 | PN25 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35366.75 | 1506.12 | 1504.92 | 1616.4095 | 163.08 | 111.4895 | 163.08 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35416.77 | 1507.46 | 1506.26 | 1616.3432 | 161.74 | 110.0832 | 161.74 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35466.82 | 1509.71 | 1508.51 | 1616.2768 | 159.49 | 107.7668 | 159.49 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35516.83 | 1510.58 | 1509.38 | 1616.2105 | 158.62 | 106.8305 | 158.62 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35566.85 | 1512.27 | 1511.07 | 1616.1442 | 156.93 | 105.0742 | 156.93 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35616.89 | 1514.29 | 1513.09 | 1616.0779 | 154.91 | 102.9879 | 154.91 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35666.92 | 1515.83 | 1514.63 | 1616.0115 | 153.37 | 101.3815 | 153.37 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35716.93 | 1517.1 | 1515.9 | 1615.9452 | 152.1 | 100.0452 | 152.1 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35766.95 | 1518.48 | 1517.28 | 1615.8789 | 150.72 | 98.5989 | 150.72 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35816.96 | 1519 | 1517.8 | 1615.8126 | 150.2 | 98.0126 | 150.2 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35866.95 | 1519.85 | 1518.65 | 1615.7463 | 149.35 | 97.0963 | 149.35 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35916.96 | 1520.56 | 1519.36 | 1615.68 | 148.64 | 96.32 | 148.64 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 35966.96 | 1520.66 | 1519.46 | 1615.6137 | 148.54 | 96.1537 | 148.54 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36016.96 | 1520.69 | 1519.49 | 1615.5474 | 148.51 | 96.0574 | 148.51 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36066.96 | 1521.01 | 1519.81 | 1615.4811 | 148.19 | 95.6711 | 148.19 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36116.96 | 1521.35 | 1520.15 | 1615.4148 | 147.85 | 95.2648 | 147.85 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36166.97 | 1522.22 | 1521.02 | 1615.3485 | 146.98 | 94.3285 | 146.98 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36216.99 | 1523.56 | 1522.36 | 1615.2822 | 145.64 | 92.9222 | 145.64 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36266.99 | 1524.5 | 1523.3 | 1615.2159 | 144.7 | 91.9159 | 144.7 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36317.32 | 1530.19 | 1528.99 | 1615.1492 | 139.01 | 86.1592 | 139.01 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36367.32 | 1530.28 | 1529.08 | 1615.0829 | 138.92 | 86.0029 | 138.92 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36417.73 | 1536.68 | 1535.48 | 1615.0161 | 132.52 | 79.5361 | 132.52 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36467.73 | 1536.65 | 1535.45 | 1614.9498 | 132.55 | 79.4998 | 132.55 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36517.94 | 1541.25 | 1540.05 | 1614.8832 | 127.95 | 74.8332 | 127.95 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36568.01 | 1544 | 1542.8 | 1614.8168 | 125.2 | 72.0168 | 125.2 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36618.07 | 1546.48 | 1545.28 | 1614.7505 | 122.72 | 69.4705 | 122.72 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36668.07 | 1546.77 | 1545.57 | 1614.6842 | 122.43 | 69.1142 | 122.43 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36718.07 | 1546.94 | 1545.74 | 1614.6179 | 122.26 | 68.8779 | 122.26 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36768.08 | 1547.09 | 1545.89 | 1614.5516 | 122.11 | 68.6616 | 122.11 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36818.08 | 1547.14 | 1545.94 | 1614.4853 | 122.06 | 68.5453 | 122.06 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36868.08 | 1547.9 | 1546.7 | 1614.419 | 121.3 | 67.719 | 121.3 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36918.08 | 1547.62 | 1546.42 | 1614.3527 | 121.58 | 67.9327 | 121.58 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 36968.08 | 1547.26 | 1546.06 | 1614.2864 | 121.94 | 68.2264 | 121.94 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37018.09 | 1547.87 | 1546.67 | 1614.2201 | 121.33 | 67.5501 | 121.33 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37068.09 | 1548.31 | 1547.11 | 1614.1538 | 120.89 | 67.0438 | 120.89 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37118.09 | 1547.99 | 1546.79 | 1614.0875 | 121.21 | 67.2975 | 121.21 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37168.09 | 1547.27 | 1546.07 | 1614.0212 | 121.93 | 67.9512 | 121.93 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37218.09 | 1547.24 | 1546.04 | 1613.9549 | 121.96 | 67.9149 | 121.96 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37268.14 | 1545.11 | 1543.91 | 1613.8886 | 124.09 | 69.9786 | 124.09 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37318.16 | 1543.68 | 1542.48 | 1613.8223 | 125.52 | 71.3423 | 125.52 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37368.18 | 1545 | 1543.8 | 1613.7559 | 124.2 | 69.9559 | 124.2 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37418.19 | 1546.07 | 1544.87 | 1613.6896 | 123.13 | 68.8196 | 123.13 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37468.19 | 1546.02 | 1544.82 | 1613.6233 | 123.18 | 68.8033 | 123.18 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37518.19 | 1545.78 | 1544.58 | 1613.557 | 123.42 | 68.977 | 123.42 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37568.19 | 1545.52 | 1544.32 | 1613.4908 | 123.68 | 69.1708 | 123.68 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37618.19 | 1545.61 | 1544.41 | 1613.4245 | 123.59 | 69.0145 | 123.59 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37668.2 | 1544.84 | 1543.64 | 1613.3582 | 124.36 | 69.7182 | 124.36 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37718.2 | 1545.12 | 1543.92 | 1613.2919 | 124.08 | 69.3719 | 124.08 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37768.22 | 1543.6 | 1542.4 | 1613.2255 | 125.6 | 70.8255 | 125.6 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37818.28 | 1541.19 | 1539.99 | 1613.1592 | 128.01 | 73.1692 | 128.01 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37868.3 | 1539.62 | 1538.42 | 1613.0929 | 129.58 | 74.6729 | 129.58 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37918.3 | 1539.71 | 1538.51 | 1613.0266 | 129.49 | 74.5166 | 129.49 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 37968.39 | 1536.73 | 1535.53 | 1612.9602 | 132.47 | 77.4302 | 132.47 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38018.43 | 1534.8 | 1533.6 | 1612.8938 | 134.4 | 79.2938 | 134.4 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38068.43 | 1534.27 | 1533.07 | 1612.8275 | 134.93 | 79.7575 | 134.93 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38118.44 | 1533.45 | 1532.25 | 1612.7612 | 135.75 | 80.5112 | 135.75 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38168.44 | 1533.92 | 1532.72 | 1612.6949 | 135.28 | 79.9749 | 135.28 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38218.45 | 1534.77 | 1533.57 | 1612.6286 | 134.43 | 79.0586 | 134.43 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38268.48 | 1536.65 | 1535.45 | 1612.5623 | 132.55 | 77.1123 | 132.55 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38318.49 | 1537.4 | 1536.2 | 1612.496 | 131.8 | 76.296 | 131.8 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38368.5 | 1538.99 | 1537.79 | 1612.4297 | 130.21 | 74.6397 | 130.21 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38418.52 | 1540.14 | 1538.94 | 1612.3634 | 129.06 | 73.4234 | 129.06 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38468.53 | 1541.28 | 1540.08 | 1612.2971 | 127.92 | 72.2171 | 127.92 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38518.54 | 1542.26 | 1541.06 | 1612.2307 | 126.94 | 71.1707 | 126.94 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38568.59 | 1544.4 | 1543.2 | 1612.1644 | 124.8 | 68.9644 | 124.8 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38618.6 | 1545.42 | 1544.22 | 1612.0981 | 123.78 | 67.8781 | 123.78 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38668.65 | 1547.62 | 1546.42 | 1612.0317 | 121.58 | 65.6117 | 121.58 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38718.65 | 1547.09 | 1545.89 | 1611.9654 | 122.11 | 66.0754 | 122.11 | PN16 | OK | yes
Z5 Ikana-Nkangamo | IKANA_NKANGAMO_GM | 38930.17 | 1555.5 | 1554.3 | 1611.685 | 113.7 | 57.385 | 113.7 | PN16 | end at tank | no
Z6 Nkangamo-Uhuru | BPS_RM_1 | 0 | 1555.5 | 1554.3 | 1738.2284 | 152.2 | 183.9284 | 183.9284 | PN25 | end at tank | no
Z6 Nkangamo-Uhuru | BPS_RM_1 | 153.17 | 1561.64 | 1560.44 | 1737.9898 | 146.06 | 177.5498 | 177.5498 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 173.18 | 1562.08 | 1560.88 | 1737.9586 | 145.62 | 177.0786 | 177.0786 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 193.2 | 1563.01 | 1561.81 | 1737.9274 | 144.69 | 176.1174 | 176.1174 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 213.21 | 1563.68 | 1562.48 | 1737.8963 | 144.02 | 175.4163 | 175.4163 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 233.23 | 1564.55 | 1563.35 | 1737.8651 | 143.15 | 174.5151 | 174.5151 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 253.24 | 1565.37 | 1564.17 | 1737.8339 | 142.33 | 173.6639 | 173.6639 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 273.25 | 1565.78 | 1564.58 | 1737.8028 | 141.92 | 173.2228 | 173.2228 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 293.26 | 1566.39 | 1565.19 | 1737.7716 | 141.31 | 172.5816 | 172.5816 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 313.26 | 1566.54 | 1565.34 | 1737.7404 | 141.16 | 172.4004 | 172.4004 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 333.27 | 1567.2 | 1566 | 1737.7093 | 140.5 | 171.7093 | 171.7093 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 353.28 | 1567.77 | 1566.57 | 1737.6781 | 139.93 | 171.1081 | 171.1081 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 373.29 | 1568.46 | 1567.26 | 1737.6469 | 139.24 | 170.3869 | 170.3869 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 393.32 | 1569.61 | 1568.41 | 1737.6157 | 138.09 | 169.2057 | 169.2057 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 413.32 | 1569.44 | 1568.24 | 1737.5846 | 138.26 | 169.3446 | 169.3446 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 433.34 | 1570.28 | 1569.08 | 1737.5534 | 137.42 | 168.4734 | 168.4734 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 453.36 | 1571.11 | 1569.91 | 1737.5222 | 136.59 | 167.6122 | 167.6122 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 473.36 | 1570.83 | 1569.63 | 1737.4911 | 136.87 | 167.8611 | 167.8611 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 493.37 | 1571.59 | 1570.39 | 1737.4599 | 136.11 | 167.0699 | 167.0699 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 513.39 | 1572.34 | 1571.14 | 1737.4287 | 135.36 | 166.2887 | 166.2887 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 533.41 | 1573.25 | 1572.05 | 1737.3975 | 134.45 | 165.3475 | 165.3475 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 553.41 | 1573.25 | 1572.05 | 1737.3664 | 134.45 | 165.3164 | 165.3164 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 573.44 | 1574.38 | 1573.18 | 1737.3352 | 133.32 | 164.1552 | 164.1552 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 593.45 | 1575.01 | 1573.81 | 1737.304 | 132.69 | 163.494 | 163.494 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 613.48 | 1576.08 | 1574.88 | 1737.2728 | 131.62 | 162.3928 | 162.3928 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 633.48 | 1576.08 | 1574.88 | 1737.2416 | 131.62 | 162.3616 | 162.3616 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 653.52 | 1577.32 | 1576.12 | 1737.2104 | 130.38 | 161.0904 | 161.0904 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 673.52 | 1577.78 | 1576.58 | 1737.1793 | 129.92 | 160.5993 | 160.5993 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 693.54 | 1578.51 | 1577.31 | 1737.1481 | 129.19 | 159.8381 | 159.8381 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 713.54 | 1578.51 | 1577.31 | 1737.1169 | 129.19 | 159.8069 | 159.8069 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 733.56 | 1579.49 | 1578.29 | 1737.0857 | 128.21 | 158.7957 | 158.7957 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 753.56 | 1579.82 | 1578.62 | 1737.0546 | 127.88 | 158.4346 | 158.4346 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 773.58 | 1580.7 | 1579.5 | 1737.0234 | 127 | 157.5234 | 157.5234 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 793.59 | 1581.4 | 1580.2 | 1736.9922 | 126.3 | 156.7922 | 156.7922 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 813.6 | 1581.53 | 1580.33 | 1736.9611 | 126.17 | 156.6311 | 156.6311 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 833.6 | 1581.72 | 1580.52 | 1736.9299 | 125.98 | 156.4099 | 156.4099 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 853.6 | 1581.76 | 1580.56 | 1736.8988 | 125.94 | 156.3388 | 156.3388 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 873.6 | 1582.14 | 1580.94 | 1736.8676 | 125.56 | 155.9276 | 155.9276 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 893.6 | 1582.03 | 1580.83 | 1736.8365 | 125.67 | 156.0065 | 156.0065 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 913.6 | 1582.05 | 1580.85 | 1736.8053 | 125.65 | 155.9553 | 155.9553 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 933.6 | 1581.82 | 1580.62 | 1736.7742 | 125.88 | 156.1542 | 156.1542 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 953.6 | 1581.68 | 1580.48 | 1736.743 | 126.02 | 156.263 | 156.263 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 973.6 | 1581.65 | 1580.45 | 1736.7118 | 126.05 | 156.2618 | 156.2618 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 993.6 | 1581.56 | 1580.36 | 1736.6807 | 126.14 | 156.3207 | 156.3207 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1013.6 | 1581.36 | 1580.16 | 1736.6495 | 126.34 | 156.4895 | 156.4895 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1033.6 | 1581.11 | 1579.91 | 1736.6184 | 126.59 | 156.7084 | 156.7084 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1053.61 | 1580.96 | 1579.76 | 1736.5872 | 126.74 | 156.8272 | 156.8272 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1073.61 | 1580.84 | 1579.64 | 1736.5561 | 126.86 | 156.9161 | 156.9161 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1093.61 | 1581.03 | 1579.83 | 1736.5249 | 126.67 | 156.6949 | 156.6949 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1112.79 | 1581.11 | 1579.91 | 1736.495 | 126.59 | 156.585 | 156.585 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1132.79 | 1580.73 | 1579.53 | 1736.4639 | 126.97 | 156.9339 | 156.9339 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1152.79 | 1580.41 | 1579.21 | 1736.4327 | 127.29 | 157.2227 | 157.2227 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1172.79 | 1580.14 | 1578.94 | 1736.4016 | 127.56 | 157.4616 | 157.4616 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1192.8 | 1579.96 | 1578.76 | 1736.3704 | 127.74 | 157.6104 | 157.6104 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1212.8 | 1579.7 | 1578.5 | 1736.3393 | 128 | 157.8393 | 157.8393 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1232.81 | 1579.01 | 1577.81 | 1736.3081 | 128.69 | 158.4981 | 158.4981 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1252.81 | 1578.87 | 1577.67 | 1736.2769 | 128.83 | 158.6069 | 158.6069 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1272.81 | 1578.68 | 1577.48 | 1736.2458 | 129.02 | 158.7658 | 158.7658 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1292.82 | 1578.1 | 1576.9 | 1736.2146 | 129.6 | 159.3146 | 159.3146 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1312.82 | 1577.86 | 1576.66 | 1736.1835 | 129.84 | 159.5235 | 159.5235 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1332.83 | 1577.31 | 1576.11 | 1736.1523 | 130.39 | 160.0423 | 160.0423 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1352.83 | 1577.01 | 1575.81 | 1736.1211 | 130.69 | 160.3111 | 160.3111 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1372.83 | 1576.71 | 1575.51 | 1736.09 | 130.99 | 160.58 | 160.58 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1392.84 | 1576.39 | 1575.19 | 1736.0588 | 131.31 | 160.8688 | 160.8688 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1412.84 | 1576.02 | 1574.82 | 1736.0277 | 131.68 | 161.2077 | 161.2077 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1432.85 | 1575.46 | 1574.26 | 1735.9965 | 132.24 | 161.7365 | 161.7365 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1452.85 | 1575.19 | 1573.99 | 1735.9653 | 132.51 | 161.9753 | 161.9753 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1472.85 | 1574.81 | 1573.61 | 1735.9342 | 132.89 | 162.3242 | 162.3242 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1492.86 | 1574.26 | 1573.06 | 1735.903 | 133.44 | 162.843 | 162.843 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1512.86 | 1573.99 | 1572.79 | 1735.8719 | 133.71 | 163.0819 | 163.0819 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1532.87 | 1573.32 | 1572.12 | 1735.8407 | 134.38 | 163.7207 | 163.7207 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1552.87 | 1573.07 | 1571.87 | 1735.8095 | 134.63 | 163.9395 | 163.9395 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1572.89 | 1572.36 | 1571.16 | 1735.7784 | 135.34 | 164.6184 | 164.6184 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1592.9 | 1571.66 | 1570.46 | 1735.7472 | 136.04 | 165.2872 | 165.2872 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1612.91 | 1571.06 | 1569.86 | 1735.716 | 136.64 | 165.856 | 165.856 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1632.92 | 1570.29 | 1569.09 | 1735.6848 | 137.41 | 166.5948 | 166.5948 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1652.93 | 1569.8 | 1568.6 | 1735.6537 | 137.9 | 167.0537 | 167.0537 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1672.96 | 1568.64 | 1567.44 | 1735.6225 | 139.06 | 168.1825 | 168.1825 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1692.96 | 1568.64 | 1567.44 | 1735.5913 | 139.06 | 168.1513 | 168.1513 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1712.99 | 1567.5 | 1566.3 | 1735.5601 | 140.2 | 169.2601 | 169.2601 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1733.03 | 1566.27 | 1565.07 | 1735.5289 | 141.43 | 170.4589 | 170.4589 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1753.05 | 1565.34 | 1564.14 | 1735.4977 | 142.36 | 171.3577 | 171.3577 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1773.05 | 1565.34 | 1564.14 | 1735.4666 | 142.36 | 171.3266 | 171.3266 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1793.08 | 1564.37 | 1563.17 | 1735.4354 | 143.33 | 172.2654 | 172.2654 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1813.13 | 1562.95 | 1561.75 | 1735.4041 | 144.75 | 173.6541 | 173.6541 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1833.13 | 1563.13 | 1561.93 | 1735.373 | 144.57 | 173.443 | 173.443 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1853.13 | 1562.91 | 1561.71 | 1735.3418 | 144.79 | 173.6318 | 173.6318 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1873.13 | 1562.88 | 1561.68 | 1735.3107 | 144.82 | 173.6307 | 173.6307 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1893.13 | 1562.83 | 1561.63 | 1735.2795 | 144.87 | 173.6495 | 173.6495 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1913.14 | 1563.29 | 1562.09 | 1735.2484 | 144.41 | 173.1584 | 173.1584 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1933.14 | 1563.09 | 1561.89 | 1735.2172 | 144.61 | 173.3272 | 173.3272 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1953.14 | 1563.13 | 1561.93 | 1735.1861 | 144.57 | 173.2561 | 173.2561 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1973.15 | 1563.82 | 1562.62 | 1735.1549 | 143.88 | 172.5349 | 172.5349 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 1993.15 | 1563.84 | 1562.64 | 1735.1237 | 143.86 | 172.4837 | 172.4837 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2013.18 | 1564.99 | 1563.79 | 1735.0925 | 142.71 | 171.3025 | 171.3025 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2033.23 | 1566.33 | 1565.13 | 1735.0613 | 141.37 | 169.9313 | 169.9313 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2053.23 | 1566.33 | 1565.13 | 1735.0301 | 141.37 | 169.9001 | 169.9001 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2073.29 | 1567.91 | 1566.71 | 1734.9989 | 139.79 | 168.2889 | 168.2889 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2093.3 | 1568.59 | 1567.39 | 1734.9677 | 139.11 | 167.5777 | 167.5777 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2113.3 | 1568.59 | 1567.39 | 1734.9366 | 139.11 | 167.5466 | 167.5466 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2133.32 | 1569.55 | 1568.35 | 1734.9054 | 138.15 | 166.5554 | 166.5554 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2153.34 | 1570.34 | 1569.14 | 1734.8742 | 137.36 | 165.7342 | 165.7342 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2173.34 | 1570.01 | 1568.81 | 1734.8431 | 137.69 | 166.0331 | 166.0331 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2193.36 | 1570.76 | 1569.56 | 1734.8119 | 136.94 | 165.2519 | 165.2519 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2213.38 | 1571.65 | 1570.45 | 1734.7807 | 136.05 | 164.3307 | 164.3307 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2233.38 | 1571.65 | 1570.45 | 1734.7495 | 136.05 | 164.2995 | 164.2995 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2253.38 | 1571.88 | 1570.68 | 1734.7184 | 135.82 | 164.0384 | 164.0384 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2273.38 | 1572.24 | 1571.04 | 1734.6872 | 135.46 | 163.6472 | 163.6472 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2293.38 | 1572.41 | 1571.21 | 1734.6561 | 135.29 | 163.4461 | 163.4461 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2313.38 | 1572.67 | 1571.47 | 1734.6249 | 135.03 | 163.1549 | 163.1549 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2333.38 | 1572.45 | 1571.25 | 1734.5938 | 135.25 | 163.3438 | 163.3438 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2353.38 | 1572.45 | 1571.25 | 1734.5626 | 135.25 | 163.3126 | 163.3126 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2373.38 | 1572.41 | 1571.21 | 1734.5315 | 135.29 | 163.3215 | 163.3215 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2393.38 | 1572.41 | 1571.21 | 1734.5003 | 135.29 | 163.2903 | 163.2903 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2413.38 | 1572.49 | 1571.29 | 1734.4692 | 135.21 | 163.1792 | 163.1792 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2433.38 | 1572.29 | 1571.09 | 1734.438 | 135.41 | 163.348 | 163.348 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2453.38 | 1572.29 | 1571.09 | 1734.4068 | 135.41 | 163.3168 | 163.3168 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2473.39 | 1572.03 | 1570.83 | 1734.3757 | 135.67 | 163.5457 | 163.5457 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2493.39 | 1572.12 | 1570.92 | 1734.3445 | 135.58 | 163.4245 | 163.4245 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2513.39 | 1572.12 | 1570.92 | 1734.3134 | 135.58 | 163.3934 | 163.3934 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2533.39 | 1572.22 | 1571.02 | 1734.2822 | 135.48 | 163.2622 | 163.2622 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2553.39 | 1572.77 | 1571.57 | 1734.2511 | 134.93 | 162.6811 | 162.6811 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2573.39 | 1572.77 | 1571.57 | 1734.2199 | 134.93 | 162.6499 | 162.6499 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2593.4 | 1573.18 | 1571.98 | 1734.1887 | 134.52 | 162.2087 | 162.2087 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2613.4 | 1573.44 | 1572.24 | 1734.1576 | 134.26 | 161.9176 | 161.9176 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2633.41 | 1574.06 | 1572.86 | 1734.1264 | 133.64 | 161.2664 | 161.2664 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2653.41 | 1574.06 | 1572.86 | 1734.0953 | 133.64 | 161.2353 | 161.2353 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2673.41 | 1574.48 | 1573.28 | 1734.0641 | 133.22 | 160.7841 | 160.7841 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2693.42 | 1574.76 | 1573.56 | 1734.0329 | 132.94 | 160.4729 | 160.4729 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2713.42 | 1574.76 | 1573.56 | 1734.0018 | 132.94 | 160.4418 | 160.4418 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2733.43 | 1575.42 | 1574.22 | 1733.9706 | 132.28 | 159.7506 | 159.7506 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2753.43 | 1575.83 | 1574.63 | 1733.9395 | 131.87 | 159.3095 | 159.3095 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2773.43 | 1575.83 | 1574.63 | 1733.9083 | 131.87 | 159.2783 | 159.2783 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2793.43 | 1575.76 | 1574.56 | 1733.8772 | 131.94 | 159.3172 | 159.3172 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2813.43 | 1575.88 | 1574.68 | 1733.846 | 131.82 | 159.166 | 159.166 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2833.43 | 1576.19 | 1574.99 | 1733.8149 | 131.51 | 158.8249 | 158.8249 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2853.44 | 1575.55 | 1574.35 | 1733.7837 | 132.15 | 159.4337 | 159.4337 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2873.45 | 1575.79 | 1574.59 | 1733.7525 | 131.91 | 159.1625 | 159.1625 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2893.45 | 1575.68 | 1574.48 | 1733.7214 | 132.02 | 159.2414 | 159.2414 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2913.45 | 1575.39 | 1574.19 | 1733.6902 | 132.31 | 159.5002 | 159.5002 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2933.45 | 1575.39 | 1574.19 | 1733.6591 | 132.31 | 159.4691 | 159.4691 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2953.45 | 1575.29 | 1574.09 | 1733.6279 | 132.41 | 159.5379 | 159.5379 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2973.45 | 1575.06 | 1573.86 | 1733.5967 | 132.64 | 159.7367 | 159.7367 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 2993.45 | 1575.39 | 1574.19 | 1733.5656 | 132.31 | 159.3756 | 159.3756 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3013.45 | 1575.62 | 1574.42 | 1733.5344 | 132.08 | 159.1144 | 159.1144 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3033.45 | 1575.7 | 1574.5 | 1733.5033 | 132 | 159.0033 | 159.0033 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3053.45 | 1575.77 | 1574.57 | 1733.4721 | 131.93 | 158.9021 | 158.9021 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3073.47 | 1576.45 | 1575.25 | 1733.441 | 131.25 | 158.191 | 158.191 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3093.5 | 1577.67 | 1576.47 | 1733.4098 | 130.03 | 156.9398 | 156.9398 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3113.5 | 1577.67 | 1576.47 | 1733.3786 | 130.03 | 156.9086 | 156.9086 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3133.59 | 1579.54 | 1578.34 | 1733.3473 | 128.16 | 155.0073 | 155.0073 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3153.64 | 1581.01 | 1579.81 | 1733.3161 | 126.69 | 153.5061 | 153.5061 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3173.65 | 1581.22 | 1580.02 | 1733.2849 | 126.48 | 153.2649 | 153.2649 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3193.69 | 1582.49 | 1581.29 | 1733.2537 | 125.21 | 151.9637 | 151.9637 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3213.73 | 1583.76 | 1582.56 | 1733.2225 | 123.94 | 150.6625 | 150.6625 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3233.74 | 1584.52 | 1583.32 | 1733.1913 | 123.18 | 149.8713 | 149.8713 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3253.77 | 1585.65 | 1584.45 | 1733.1601 | 122.05 | 148.7101 | 148.7101 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3273.77 | 1585.65 | 1584.45 | 1733.129 | 122.05 | 148.679 | 148.679 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3293.79 | 1586.5 | 1585.3 | 1733.0978 | 121.2 | 147.7978 | 147.7978 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3313.79 | 1586.5 | 1585.3 | 1733.0666 | 121.2 | 147.7666 | 147.7666 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3333.8 | 1587.2 | 1586 | 1733.0354 | 120.5 | 147.0354 | 147.0354 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3353.8 | 1587.48 | 1586.28 | 1733.0043 | 120.22 | 146.7243 | 146.7243 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3373.81 | 1587.9 | 1586.7 | 1732.9731 | 119.8 | 146.2731 | 146.2731 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3393.81 | 1587.9 | 1586.7 | 1732.942 | 119.8 | 146.242 | 146.242 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3413.81 | 1588.25 | 1587.05 | 1732.9108 | 119.45 | 145.8608 | 145.8608 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3433.81 | 1588.25 | 1587.05 | 1732.8797 | 119.45 | 145.8297 | 145.8297 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3453.81 | 1588.16 | 1586.96 | 1732.8485 | 119.54 | 145.8885 | 145.8885 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3473.81 | 1588.02 | 1586.82 | 1732.8174 | 119.68 | 145.9974 | 145.9974 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3493.81 | 1588.27 | 1587.07 | 1732.7862 | 119.43 | 145.7162 | 145.7162 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3513.83 | 1589.11 | 1587.91 | 1732.755 | 118.59 | 144.845 | 144.845 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3533.84 | 1588.52 | 1587.32 | 1732.7238 | 119.18 | 145.4038 | 145.4038 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3553.84 | 1588.12 | 1586.92 | 1732.6927 | 119.58 | 145.7727 | 145.7727 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3573.86 | 1588.87 | 1587.67 | 1732.6615 | 118.83 | 144.9915 | 144.9915 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3593.86 | 1588.81 | 1587.61 | 1732.6304 | 118.89 | 145.0204 | 145.0204 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3613.86 | 1588.55 | 1587.35 | 1732.5992 | 119.15 | 145.2492 | 145.2492 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3633.89 | 1589.65 | 1588.45 | 1732.568 | 118.05 | 144.118 | 144.118 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3653.9 | 1589.07 | 1587.87 | 1732.5368 | 118.63 | 144.6668 | 144.6668 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3673.91 | 1588.41 | 1587.21 | 1732.5057 | 119.29 | 145.2957 | 145.2957 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3693.95 | 1589.75 | 1588.55 | 1732.4745 | 117.95 | 143.9245 | 143.9245 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3713.98 | 1588.65 | 1587.45 | 1732.4433 | 119.05 | 144.9933 | 144.9933 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3734 | 1589.37 | 1588.17 | 1732.4121 | 118.33 | 144.2421 | 144.2421 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3754 | 1589.38 | 1588.18 | 1732.3809 | 118.32 | 144.2009 | 144.2009 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3774 | 1589.37 | 1588.17 | 1732.3498 | 118.33 | 144.1798 | 144.1798 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3794 | 1589.72 | 1588.52 | 1732.3186 | 117.98 | 143.7986 | 143.7986 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3814.01 | 1589.3 | 1588.1 | 1732.2874 | 118.4 | 144.1874 | 144.1874 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3834.03 | 1590.22 | 1589.02 | 1732.2563 | 117.48 | 143.2363 | 143.2363 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3854.04 | 1589.58 | 1588.38 | 1732.2251 | 118.12 | 143.8451 | 143.8451 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3874.04 | 1589.46 | 1588.26 | 1732.1939 | 118.24 | 143.9339 | 143.9339 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3894.04 | 1589.25 | 1588.05 | 1732.1628 | 118.45 | 144.1128 | 144.1128 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3914.06 | 1588.29 | 1587.09 | 1732.1316 | 119.41 | 145.0416 | 145.0416 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3934.06 | 1588.32 | 1587.12 | 1732.1004 | 119.38 | 144.9804 | 144.9804 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3954.08 | 1587.36 | 1586.16 | 1732.0693 | 120.34 | 145.9093 | 145.9093 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3974.08 | 1587.29 | 1586.09 | 1732.0381 | 120.41 | 145.9481 | 145.9481 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 3994.1 | 1586.46 | 1585.26 | 1732.0069 | 121.24 | 146.7469 | 146.7469 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4014.14 | 1585.24 | 1584.04 | 1731.9757 | 122.46 | 147.9357 | 147.9357 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4034.25 | 1583.14 | 1581.94 | 1731.9444 | 124.56 | 150.0044 | 150.0044 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4054.29 | 1584.38 | 1583.18 | 1731.9132 | 123.32 | 148.7332 | 148.7332 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4074.34 | 1585.79 | 1584.59 | 1731.8819 | 121.91 | 147.2919 | 147.2919 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4094.35 | 1586.54 | 1585.34 | 1731.8508 | 121.16 | 146.5108 | 146.5108 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4114.35 | 1586.3 | 1585.1 | 1731.8196 | 121.4 | 146.7196 | 146.7196 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4134.39 | 1587.46 | 1586.26 | 1731.7884 | 120.24 | 145.5284 | 145.5284 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4154.41 | 1588.37 | 1587.17 | 1731.7572 | 119.33 | 144.5872 | 144.5872 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4174.41 | 1588.34 | 1587.14 | 1731.7261 | 119.36 | 144.5861 | 144.5861 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4194.43 | 1589.26 | 1588.06 | 1731.6949 | 118.44 | 143.6349 | 143.6349 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4214.45 | 1590.24 | 1589.04 | 1731.6637 | 117.46 | 142.6237 | 142.6237 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4234.45 | 1589.92 | 1588.72 | 1731.6325 | 117.78 | 142.9125 | 142.9125 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4254.46 | 1590.3 | 1589.1 | 1731.6014 | 117.4 | 142.5014 | 142.5014 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4274.47 | 1590.88 | 1589.68 | 1731.5702 | 116.82 | 141.8902 | 141.8902 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4294.47 | 1590.5 | 1589.3 | 1731.539 | 117.2 | 142.239 | 142.239 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4314.47 | 1590.23 | 1589.03 | 1731.5079 | 117.47 | 142.4779 | 142.4779 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4334.48 | 1590.67 | 1589.47 | 1731.4767 | 117.03 | 142.0067 | 142.0067 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4354.48 | 1590.45 | 1589.25 | 1731.4456 | 117.25 | 142.1956 | 142.1956 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4374.48 | 1590.23 | 1589.03 | 1731.4144 | 117.47 | 142.3844 | 142.3844 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4394.49 | 1589.65 | 1588.45 | 1731.3832 | 118.05 | 142.9332 | 142.9332 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4414.49 | 1589.15 | 1587.95 | 1731.3521 | 118.55 | 143.4021 | 143.4021 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4434.5 | 1589.65 | 1588.45 | 1731.3209 | 118.05 | 142.8709 | 142.8709 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4454.52 | 1588.67 | 1587.47 | 1731.2897 | 119.03 | 143.8197 | 143.8197 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4474.53 | 1588.24 | 1587.04 | 1731.2586 | 119.46 | 144.2186 | 144.2186 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4494.53 | 1588.14 | 1586.94 | 1731.2274 | 119.56 | 144.2874 | 144.2874 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4514.6 | 1586.46 | 1585.26 | 1731.1962 | 121.24 | 145.9362 | 145.9362 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4534.61 | 1587.06 | 1585.86 | 1731.165 | 120.64 | 145.305 | 145.305 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4554.61 | 1587.08 | 1585.88 | 1731.1338 | 120.62 | 145.2538 | 145.2538 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4574.64 | 1585.89 | 1584.69 | 1731.1026 | 121.81 | 146.4126 | 146.4126 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4594.64 | 1585.92 | 1584.72 | 1731.0715 | 121.78 | 146.3515 | 146.3515 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4614.67 | 1584.89 | 1583.69 | 1731.0403 | 122.81 | 147.3503 | 147.3503 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4634.7 | 1583.76 | 1582.56 | 1731.0091 | 123.94 | 148.4491 | 148.4491 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4654.71 | 1583.36 | 1582.16 | 1730.9779 | 124.34 | 148.8179 | 148.8179 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4674.72 | 1582.71 | 1581.51 | 1730.9467 | 124.99 | 149.4367 | 149.4367 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4694.72 | 1582.29 | 1581.09 | 1730.9156 | 125.41 | 149.8256 | 149.8256 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4714.79 | 1580.61 | 1579.41 | 1730.8843 | 127.09 | 151.4743 | 151.4743 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4734.8 | 1580 | 1578.8 | 1730.8532 | 127.7 | 152.0532 | 152.0532 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4754.84 | 1578.75 | 1577.55 | 1730.8219 | 128.95 | 153.2719 | 153.2719 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4774.88 | 1577.47 | 1576.27 | 1730.7907 | 130.23 | 154.5207 | 154.5207 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4794.88 | 1577.12 | 1575.92 | 1730.7596 | 130.58 | 154.8396 | 154.8396 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4814.97 | 1575.31 | 1574.11 | 1730.7283 | 132.39 | 156.6183 | 156.6183 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4835.01 | 1576.7 | 1575.5 | 1730.6971 | 131 | 155.1971 | 155.1971 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4855.01 | 1576.6 | 1575.4 | 1730.6659 | 131.1 | 155.2659 | 155.2659 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4875.04 | 1577.66 | 1576.46 | 1730.6347 | 130.04 | 154.1747 | 154.1747 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4895.06 | 1578.6 | 1577.4 | 1730.6035 | 129.1 | 153.2035 | 153.2035 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4915.06 | 1578.48 | 1577.28 | 1730.5724 | 129.22 | 153.2924 | 153.2924 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4935.09 | 1579.49 | 1578.29 | 1730.5412 | 128.21 | 152.2512 | 152.2512 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4955.13 | 1578.23 | 1577.03 | 1730.51 | 129.47 | 153.48 | 153.48 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4975.14 | 1578.88 | 1577.68 | 1730.4788 | 128.82 | 152.7988 | 152.7988 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 4995.15 | 1579.34 | 1578.14 | 1730.4476 | 128.36 | 152.3076 | 152.3076 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5015.15 | 1578.94 | 1577.74 | 1730.4165 | 128.76 | 152.6765 | 152.6765 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5035.16 | 1579.68 | 1578.48 | 1730.3853 | 128.02 | 151.9053 | 151.9053 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5055.19 | 1578.72 | 1577.52 | 1730.3541 | 128.98 | 152.8341 | 152.8341 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5075.2 | 1579.47 | 1578.27 | 1730.3229 | 128.23 | 152.0529 | 152.0529 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5095.21 | 1578.85 | 1577.65 | 1730.2918 | 128.85 | 152.6418 | 152.6418 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5115.22 | 1579.58 | 1578.38 | 1730.2606 | 128.12 | 151.8806 | 151.8806 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5135.25 | 1578.5 | 1577.3 | 1730.2294 | 129.2 | 152.9294 | 152.9294 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5155.25 | 1578.33 | 1577.13 | 1730.1982 | 129.37 | 153.0682 | 153.0682 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5175.26 | 1577.87 | 1576.67 | 1730.1671 | 129.83 | 153.4971 | 153.4971 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5195.26 | 1577.37 | 1576.17 | 1730.1359 | 130.33 | 153.9659 | 153.9659 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5215.27 | 1577.01 | 1575.81 | 1730.1047 | 130.69 | 154.2947 | 154.2947 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5235.27 | 1576.49 | 1575.29 | 1730.0736 | 131.21 | 154.7836 | 154.7836 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5255.28 | 1576.24 | 1575.04 | 1730.0424 | 131.46 | 155.0024 | 155.0024 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5275.28 | 1575.85 | 1574.65 | 1730.0113 | 131.85 | 155.3613 | 155.3613 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5295.28 | 1575.7 | 1574.5 | 1729.9801 | 132 | 155.4801 | 155.4801 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5315.28 | 1575.54 | 1574.34 | 1729.949 | 132.16 | 155.609 | 155.609 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5335.3 | 1574.77 | 1573.57 | 1729.9178 | 132.93 | 156.3478 | 156.3478 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5355.3 | 1574.25 | 1573.05 | 1729.8866 | 133.45 | 156.8366 | 156.8366 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5375.31 | 1573.59 | 1572.39 | 1729.8555 | 134.11 | 157.4655 | 157.4655 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5395.33 | 1572.8 | 1571.6 | 1729.8243 | 134.9 | 158.2243 | 158.2243 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5415.36 | 1571.75 | 1570.55 | 1729.7931 | 135.95 | 159.2431 | 159.2431 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5435.36 | 1571.8 | 1570.6 | 1729.7619 | 135.9 | 159.1619 | 159.1619 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5455.43 | 1570.14 | 1568.94 | 1729.7307 | 137.56 | 160.7907 | 160.7907 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5475.43 | 1569.65 | 1568.45 | 1729.6995 | 138.05 | 161.2495 | 161.2495 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5495.47 | 1568.41 | 1567.21 | 1729.6683 | 139.29 | 162.4583 | 162.4583 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5515.49 | 1567.57 | 1566.37 | 1729.6371 | 140.13 | 163.2671 | 163.2671 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5535.52 | 1566.44 | 1565.24 | 1729.6059 | 141.26 | 164.3659 | 164.3659 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5555.57 | 1565.07 | 1563.87 | 1729.5747 | 142.63 | 165.7047 | 165.7047 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5575.61 | 1563.73 | 1562.53 | 1729.5435 | 143.97 | 167.0135 | 167.0135 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5595.67 | 1562.15 | 1560.95 | 1729.5122 | 145.55 | 168.5622 | 168.5622 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5615.67 | 1562.14 | 1560.94 | 1729.4811 | 145.56 | 168.5411 | 168.5411 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5635.68 | 1561.57 | 1560.37 | 1729.4499 | 146.13 | 169.0799 | 169.0799 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5655.88 | 1564.38 | 1563.18 | 1729.4184 | 143.32 | 166.2384 | 166.2384 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5675.89 | 1565.16 | 1563.96 | 1729.3873 | 142.54 | 165.4273 | 165.4273 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5695.91 | 1565.87 | 1564.67 | 1729.3561 | 141.83 | 164.6861 | 164.6861 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5715.91 | 1565.64 | 1564.44 | 1729.3249 | 142.06 | 164.8849 | 164.8849 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5735.91 | 1565.43 | 1564.23 | 1729.2938 | 142.27 | 165.0638 | 165.0638 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5755.91 | 1565.88 | 1564.68 | 1729.2626 | 141.82 | 164.5826 | 164.5826 | PN25 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5776.05 | 1568.24 | 1567.04 | 1729.2312 | 139.46 | 162.1912 | 162.1912 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5796.05 | 1568.01 | 1566.81 | 1729.2001 | 139.69 | 162.3901 | 162.3901 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5816.07 | 1568.94 | 1567.74 | 1729.1689 | 138.76 | 161.4289 | 161.4289 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5836.1 | 1569.86 | 1568.66 | 1729.1377 | 137.84 | 160.4777 | 160.4777 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5856.1 | 1570.3 | 1569.1 | 1729.1065 | 137.4 | 160.0065 | 160.0065 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5876.13 | 1571.32 | 1570.12 | 1729.0753 | 136.38 | 158.9553 | 158.9553 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5896.16 | 1570.12 | 1568.92 | 1729.0441 | 137.58 | 160.1241 | 160.1241 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5916.23 | 1571.73 | 1570.53 | 1729.0129 | 135.97 | 158.4829 | 158.4829 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5936.23 | 1572 | 1570.8 | 1728.9817 | 135.7 | 158.1817 | 158.1817 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5956.25 | 1572.96 | 1571.76 | 1728.9505 | 134.74 | 157.1905 | 157.1905 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5976.26 | 1573.53 | 1572.33 | 1728.9194 | 134.17 | 156.5894 | 156.5894 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 5996.27 | 1574.07 | 1572.87 | 1728.8882 | 133.63 | 156.0182 | 156.0182 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6016.27 | 1573.9 | 1572.7 | 1728.8571 | 133.8 | 156.1571 | 156.1571 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6036.27 | 1573.97 | 1572.77 | 1728.8259 | 133.73 | 156.0559 | 156.0559 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6056.29 | 1574.87 | 1573.67 | 1728.7947 | 132.83 | 155.1247 | 155.1247 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6076.39 | 1572.83 | 1571.63 | 1728.7634 | 134.87 | 157.1334 | 157.1334 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6096.52 | 1575.05 | 1573.85 | 1728.7321 | 132.65 | 154.8821 | 154.8821 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6116.53 | 1574.4 | 1573.2 | 1728.7009 | 133.3 | 155.5009 | 155.5009 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6136.6 | 1576.1 | 1574.9 | 1728.6696 | 131.6 | 153.7696 | 153.7696 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6156.6 | 1576.06 | 1574.86 | 1728.6385 | 131.64 | 153.7785 | 153.7785 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6176.6 | 1576.2 | 1575 | 1728.6073 | 131.5 | 153.6073 | 153.6073 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6196.6 | 1576.01 | 1574.81 | 1728.5762 | 131.69 | 153.7662 | 153.7662 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6216.65 | 1577.36 | 1576.16 | 1728.5449 | 130.34 | 152.3849 | 152.3849 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6236.76 | 1575.24 | 1574.04 | 1728.5136 | 132.46 | 154.4736 | 154.4736 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6256.76 | 1575.44 | 1574.24 | 1728.4825 | 132.26 | 154.2425 | 154.2425 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6276.78 | 1574.56 | 1573.36 | 1728.4513 | 133.14 | 155.0913 | 155.0913 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6296.79 | 1575.26 | 1574.06 | 1728.4201 | 132.44 | 154.3601 | 154.3601 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6316.83 | 1576.48 | 1575.28 | 1728.3889 | 131.22 | 153.1089 | 153.1089 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6336.85 | 1577.46 | 1576.26 | 1728.3577 | 130.24 | 152.0977 | 152.0977 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6356.92 | 1579.12 | 1577.92 | 1728.3264 | 128.58 | 150.4064 | 150.4064 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6376.95 | 1580.15 | 1578.95 | 1728.2952 | 127.55 | 149.3452 | 149.3452 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6396.97 | 1581.16 | 1579.96 | 1728.2641 | 126.54 | 148.3041 | 148.3041 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6416.98 | 1580.67 | 1579.47 | 1728.2329 | 127.03 | 148.7629 | 148.7629 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6436.98 | 1580.8 | 1579.6 | 1728.2017 | 126.9 | 148.6017 | 148.6017 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6456.98 | 1580.62 | 1579.42 | 1728.1706 | 127.08 | 148.7506 | 148.7506 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6476.98 | 1580.55 | 1579.35 | 1728.1394 | 127.15 | 148.7894 | 148.7894 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6497 | 1581.38 | 1580.18 | 1728.1082 | 126.32 | 147.9282 | 147.9282 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6517.08 | 1583.25 | 1582.05 | 1728.077 | 124.45 | 146.027 | 146.027 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6537.11 | 1584.27 | 1583.07 | 1728.0458 | 123.43 | 144.9758 | 144.9758 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6557.17 | 1585.85 | 1584.65 | 1728.0145 | 121.85 | 143.3645 | 143.3645 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6577.24 | 1587.5 | 1586.3 | 1727.9833 | 120.2 | 141.6833 | 141.6833 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6597.29 | 1588.85 | 1587.65 | 1727.952 | 118.85 | 140.302 | 140.302 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6617.41 | 1591.05 | 1589.85 | 1727.9207 | 116.65 | 138.0707 | 138.0707 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6637.44 | 1592.24 | 1591.04 | 1727.8895 | 115.46 | 136.8495 | 136.8495 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6657.47 | 1593.39 | 1592.19 | 1727.8583 | 114.31 | 135.6683 | 135.6683 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6677.66 | 1596.15 | 1594.95 | 1727.8268 | 111.55 | 132.8768 | 132.8768 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6697.72 | 1594.68 | 1593.48 | 1727.7956 | 113.02 | 134.3156 | 134.3156 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6717.76 | 1595.93 | 1594.73 | 1727.7644 | 111.77 | 133.0344 | 133.0344 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6737.76 | 1596.36 | 1595.16 | 1727.7332 | 111.34 | 132.5732 | 132.5732 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6757.77 | 1597.04 | 1595.84 | 1727.702 | 110.66 | 131.862 | 131.862 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6777.79 | 1597.97 | 1596.77 | 1727.6709 | 109.73 | 130.9009 | 130.9009 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6797.8 | 1598.3 | 1597.1 | 1727.6397 | 109.4 | 130.5397 | 130.5397 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6817.81 | 1598.93 | 1597.73 | 1727.6085 | 108.77 | 129.8785 | 129.8785 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6837.81 | 1599.32 | 1598.12 | 1727.5774 | 108.38 | 129.4574 | 129.4574 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6857.82 | 1599.86 | 1598.66 | 1727.5462 | 107.84 | 128.8862 | 128.8862 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6877.82 | 1600.26 | 1599.06 | 1727.515 | 107.44 | 128.455 | 128.455 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6898.06 | 1600.6 | 1599.4 | 1727.4835 | 107.1 | 128.0835 | 128.0835 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6918.06 | 1600.25 | 1599.05 | 1727.4524 | 107.45 | 128.4024 | 128.4024 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6938.06 | 1600.35 | 1599.15 | 1727.4212 | 107.35 | 128.2712 | 128.2712 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6958.06 | 1600.39 | 1599.19 | 1727.3901 | 107.31 | 128.2001 | 128.2001 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6978.06 | 1600.71 | 1599.51 | 1727.3589 | 106.99 | 127.8489 | 127.8489 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 6998.06 | 1600.7 | 1599.5 | 1727.3278 | 107 | 127.8278 | 127.8278 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7017.3 | 1601.45 | 1600.25 | 1727.2978 | 106.25 | 127.0478 | 127.0478 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7037.34 | 1602.8 | 1601.6 | 1727.2666 | 104.9 | 125.6666 | 125.6666 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7057.34 | 1602.88 | 1601.68 | 1727.2354 | 104.82 | 125.5554 | 125.5554 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7077.4 | 1604.4 | 1603.2 | 1727.2042 | 103.3 | 124.0042 | 124.0042 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7097.41 | 1605.05 | 1603.85 | 1727.173 | 102.65 | 123.323 | 123.323 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7117.42 | 1605.75 | 1604.55 | 1727.1418 | 101.95 | 122.5918 | 122.5918 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7137.44 | 1606.62 | 1605.42 | 1727.1106 | 101.08 | 121.6906 | 121.6906 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7157.45 | 1607.17 | 1605.97 | 1727.0795 | 100.53 | 121.1095 | 121.1095 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7177.49 | 1608.45 | 1607.25 | 1727.0483 | 99.25 | 119.7983 | 119.7983 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7197.5 | 1608.97 | 1607.77 | 1727.0171 | 98.73 | 119.2471 | 119.2471 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7217.52 | 1609.97 | 1608.77 | 1726.9859 | 97.73 | 118.2159 | 118.2159 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7237.52 | 1610.33 | 1609.13 | 1726.9548 | 97.37 | 117.8248 | 117.8248 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7257.54 | 1611.07 | 1609.87 | 1726.9236 | 96.63 | 117.0536 | 117.0536 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7277.54 | 1611.39 | 1610.19 | 1726.8924 | 96.31 | 116.7024 | 116.7024 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7297.56 | 1612.26 | 1611.06 | 1726.8612 | 95.44 | 115.8012 | 115.8012 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7317.56 | 1612.17 | 1610.97 | 1726.8301 | 95.53 | 115.8601 | 115.8601 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7337.56 | 1612.57 | 1611.37 | 1726.7989 | 95.13 | 115.4289 | 115.4289 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7357.6 | 1613.8 | 1612.6 | 1726.7677 | 93.9 | 114.1677 | 114.1677 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7377.62 | 1614.6 | 1613.4 | 1726.7365 | 93.1 | 113.3365 | 113.3365 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7397.86 | 1616.22 | 1615.02 | 1726.705 | 91.48 | 111.685 | 111.685 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7417.86 | 1616.1 | 1614.9 | 1726.6738 | 91.6 | 111.7738 | 111.7738 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7437.94 | 1617.87 | 1616.67 | 1726.6426 | 89.83 | 109.9726 | 109.9726 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7458.04 | 1619.9 | 1618.7 | 1726.6113 | 87.8 | 107.9113 | 107.9113 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7478.09 | 1621.29 | 1620.09 | 1726.58 | 86.41 | 106.49 | 106.49 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7498.14 | 1622.72 | 1621.52 | 1726.5488 | 84.98 | 105.0288 | 105.0288 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7518.16 | 1623.45 | 1622.25 | 1726.5176 | 84.25 | 104.2676 | 104.2676 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7538.2 | 1624.71 | 1623.51 | 1726.4864 | 82.99 | 102.9764 | 102.9764 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7558.33 | 1627 | 1625.8 | 1726.455 | 80.7 | 100.655 | 100.655 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7578.36 | 1628.17 | 1626.97 | 1726.4238 | 79.53 | 99.4538 | 99.4538 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7598.44 | 1629.92 | 1628.72 | 1726.3926 | 77.78 | 97.6726 | 97.6726 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7618.55 | 1632.02 | 1630.82 | 1726.3612 | 75.68 | 95.5412 | 95.5412 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7638.58 | 1633.2 | 1632 | 1726.33 | 74.5 | 94.33 | 94.33 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7658.63 | 1634.63 | 1633.43 | 1726.2988 | 73.07 | 92.8688 | 92.8688 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7678.65 | 1635.51 | 1634.31 | 1726.2676 | 72.19 | 91.9576 | 91.9576 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7698.71 | 1637.04 | 1635.84 | 1726.2364 | 70.66 | 90.3964 | 90.3964 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7718.72 | 1637.61 | 1636.41 | 1726.2052 | 70.09 | 89.7952 | 89.7952 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7738.75 | 1638.76 | 1637.56 | 1726.174 | 68.94 | 88.614 | 88.614 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7758.77 | 1639.59 | 1638.39 | 1726.1428 | 68.11 | 87.7528 | 87.7528 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7778.79 | 1640.58 | 1639.38 | 1726.1116 | 67.12 | 86.7316 | 86.7316 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7798.8 | 1640.84 | 1639.64 | 1726.0805 | 66.86 | 86.4405 | 86.4405 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7818.82 | 1641.85 | 1640.65 | 1726.0493 | 65.85 | 85.3993 | 85.3993 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7838.82 | 1641.85 | 1640.65 | 1726.0181 | 65.85 | 85.3681 | 85.3681 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7858.84 | 1642.69 | 1641.49 | 1725.9869 | 65.01 | 84.4969 | 84.4969 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7878.85 | 1643.43 | 1642.23 | 1725.9558 | 64.27 | 83.7258 | 83.7258 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7898.85 | 1643.44 | 1642.24 | 1725.9246 | 64.26 | 83.6846 | 83.6846 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7918.86 | 1643.95 | 1642.75 | 1725.8935 | 63.75 | 83.1435 | 83.1435 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7938.87 | 1644.5 | 1643.3 | 1725.8623 | 63.2 | 82.5623 | 82.5623 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7958.87 | 1644.85 | 1643.65 | 1725.8311 | 62.85 | 82.1811 | 82.1811 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7978.87 | 1645.06 | 1643.86 | 1725.8 | 62.64 | 81.94 | 81.94 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 7998.87 | 1645.34 | 1644.14 | 1725.7688 | 62.36 | 81.6288 | 81.6288 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8018.88 | 1645.99 | 1644.79 | 1725.7377 | 61.71 | 80.9477 | 80.9477 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8038.88 | 1646.23 | 1645.03 | 1725.7065 | 61.47 | 80.6765 | 80.6765 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8058.89 | 1646.88 | 1645.68 | 1725.6753 | 60.82 | 79.9953 | 79.9953 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8078.9 | 1646.57 | 1645.37 | 1725.6442 | 61.13 | 80.2742 | 80.2742 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8098.9 | 1647 | 1645.8 | 1725.613 | 60.7 | 79.813 | 79.813 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8118.91 | 1647.51 | 1646.31 | 1725.5818 | 60.19 | 79.2718 | 79.2718 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8138.91 | 1647.85 | 1646.65 | 1725.5507 | 59.85 | 78.9007 | 78.9007 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8158.92 | 1648.37 | 1647.17 | 1725.5195 | 59.33 | 78.3495 | 78.3495 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8178.93 | 1649.09 | 1647.89 | 1725.4884 | 58.61 | 77.5984 | 77.5984 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8198.93 | 1648.97 | 1647.77 | 1725.4572 | 58.73 | 77.6872 | 77.6872 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8218.93 | 1649.22 | 1648.02 | 1725.426 | 58.48 | 77.406 | 77.406 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8238.94 | 1649.82 | 1648.62 | 1725.3949 | 57.88 | 76.7749 | 76.7749 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8258.95 | 1650.26 | 1649.06 | 1725.3637 | 57.44 | 76.3037 | 76.3037 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8278.95 | 1650.35 | 1649.15 | 1725.3326 | 57.35 | 76.1826 | 76.1826 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8298.95 | 1650.75 | 1649.55 | 1725.3014 | 56.95 | 75.7514 | 75.7514 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8318.95 | 1651.11 | 1649.91 | 1725.2703 | 56.59 | 75.3603 | 75.3603 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8338.96 | 1651.6 | 1650.4 | 1725.2391 | 56.1 | 74.8391 | 74.8391 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8358.96 | 1651.8 | 1650.6 | 1725.2079 | 55.9 | 74.6079 | 74.6079 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8378.96 | 1652.05 | 1650.85 | 1725.1768 | 55.65 | 74.3268 | 74.3268 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8398.97 | 1652.54 | 1651.34 | 1725.1456 | 55.16 | 73.8056 | 73.8056 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8418.97 | 1652.93 | 1651.73 | 1725.1145 | 54.77 | 73.3845 | 73.3845 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8439.03 | 1653.77 | 1652.57 | 1725.0832 | 53.93 | 72.5132 | 72.5132 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8459.08 | 1655.13 | 1653.93 | 1725.052 | 52.57 | 71.122 | 71.122 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8479.08 | 1655.27 | 1654.07 | 1725.0208 | 52.43 | 70.9508 | 70.9508 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8499.09 | 1655.88 | 1654.68 | 1724.9897 | 51.82 | 70.3097 | 70.3097 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8519.12 | 1657.08 | 1655.88 | 1724.9585 | 50.62 | 69.0785 | 69.0785 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8539.14 | 1657.9 | 1656.7 | 1724.9273 | 49.8 | 68.2273 | 68.2273 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8559.15 | 1658.51 | 1657.31 | 1724.8961 | 49.19 | 67.5861 | 67.5861 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8579.15 | 1658.91 | 1657.71 | 1724.8649 | 48.79 | 67.1549 | 67.1549 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8599.15 | 1659.09 | 1657.89 | 1724.8338 | 48.61 | 66.9438 | 66.9438 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8619.17 | 1659.88 | 1658.68 | 1724.8026 | 47.82 | 66.1226 | 66.1226 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8639.18 | 1660.55 | 1659.35 | 1724.7714 | 47.15 | 65.4214 | 65.4214 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8659.25 | 1662.17 | 1660.97 | 1724.7402 | 45.53 | 63.7702 | 63.7702 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8679.25 | 1662.42 | 1661.22 | 1724.709 | 45.28 | 63.489 | 63.489 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8699.26 | 1663.27 | 1662.07 | 1724.6779 | 44.43 | 62.6079 | 62.6079 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8719.29 | 1664.29 | 1663.09 | 1724.6467 | 43.41 | 61.5567 | 61.5567 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8739.29 | 1664.61 | 1663.41 | 1724.6155 | 43.09 | 61.2055 | 61.2055 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8759.32 | 1665.69 | 1664.49 | 1724.5843 | 42.01 | 60.0943 | 60.0943 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8779.32 | 1665.96 | 1664.76 | 1724.5531 | 41.74 | 59.7931 | 59.7931 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8799.34 | 1666.75 | 1665.55 | 1724.522 | 40.95 | 58.972 | 58.972 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8819.37 | 1667.8 | 1666.6 | 1724.4908 | 39.9 | 57.8908 | 57.8908 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8839.39 | 1668.65 | 1667.45 | 1724.4596 | 39.05 | 57.0096 | 57.0096 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8859.41 | 1669.53 | 1668.33 | 1724.4284 | 38.17 | 56.0984 | 56.0984 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8879.42 | 1670.32 | 1669.12 | 1724.3972 | 37.38 | 55.2772 | 55.2772 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8899.43 | 1670.78 | 1669.58 | 1724.3661 | 36.92 | 54.7861 | 54.7861 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8919.45 | 1671.69 | 1670.49 | 1724.3349 | 36.01 | 53.8449 | 53.8449 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8939.47 | 1672.55 | 1671.35 | 1724.3037 | 35.15 | 52.9537 | 52.9537 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8959.47 | 1672.95 | 1671.75 | 1724.2725 | 34.75 | 52.5225 | 52.5225 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8979.49 | 1673.77 | 1672.57 | 1724.2414 | 33.93 | 51.6714 | 51.6714 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 8999.51 | 1674.73 | 1673.53 | 1724.2102 | 32.97 | 50.6802 | 50.6802 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9019.51 | 1675.09 | 1673.89 | 1724.179 | 32.61 | 50.289 | 50.289 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9039.52 | 1675.58 | 1674.38 | 1724.1478 | 32.12 | 49.7678 | 49.7678 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9059.54 | 1676.51 | 1675.31 | 1724.1167 | 31.19 | 48.8067 | 48.8067 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9079.56 | 1677.45 | 1676.25 | 1724.0855 | 30.25 | 47.8355 | 47.8355 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9099.57 | 1677.81 | 1676.61 | 1724.0543 | 29.89 | 47.4443 | 47.4443 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9119.59 | 1678.86 | 1677.66 | 1724.0231 | 28.84 | 46.3631 | 46.3631 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9139.59 | 1679.14 | 1677.94 | 1723.992 | 28.56 | 46.052 | 46.052 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9159.61 | 1679.84 | 1678.64 | 1723.9608 | 27.86 | 45.3208 | 45.3208 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9179.62 | 1680.48 | 1679.28 | 1723.9296 | 27.22 | 44.6496 | 44.6496 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9199.62 | 1680.98 | 1679.78 | 1723.8985 | 26.72 | 44.1185 | 44.1185 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9219.63 | 1681.38 | 1680.18 | 1723.8673 | 26.32 | 43.6873 | 43.6873 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9239.64 | 1682.19 | 1680.99 | 1723.8361 | 25.51 | 42.8461 | 42.8461 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9259.67 | 1683.3 | 1682.1 | 1723.8049 | 24.4 | 41.7049 | 41.7049 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9275.48 | 1684.06 | 1682.86 | 1723.7803 | 23.64 | 40.9203 | 40.9203 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9295.52 | 1682.87 | 1681.67 | 1723.7491 | 24.83 | 42.0791 | 42.0791 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9315.52 | 1682.89 | 1681.69 | 1723.7179 | 24.81 | 42.0279 | 42.0279 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9335.52 | 1682.74 | 1681.54 | 1723.6868 | 24.96 | 42.1468 | 42.1468 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9355.58 | 1684.26 | 1683.06 | 1723.6555 | 23.44 | 40.5955 | 40.5955 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9375.59 | 1683.56 | 1682.36 | 1723.6244 | 24.14 | 41.2644 | 41.2644 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9395.6 | 1684.36 | 1683.16 | 1723.5932 | 23.34 | 40.4332 | 40.4332 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9415.64 | 1683.19 | 1681.99 | 1723.562 | 24.51 | 41.572 | 41.572 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9435.64 | 1683.32 | 1682.12 | 1723.5308 | 24.38 | 41.4108 | 41.4108 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9455.64 | 1683.49 | 1682.29 | 1723.4997 | 24.21 | 41.2097 | 41.2097 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9475.86 | 1683.39 | 1682.19 | 1723.4682 | 24.31 | 41.2782 | 41.2782 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9495.86 | 1683.66 | 1682.46 | 1723.437 | 24.04 | 40.977 | 40.977 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9515.87 | 1683.19 | 1681.99 | 1723.4059 | 24.51 | 41.4159 | 41.4159 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9535.93 | 1684.79 | 1683.59 | 1723.3746 | 22.91 | 39.7846 | 39.7846 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9555.96 | 1683.81 | 1682.61 | 1723.3434 | 23.89 | 40.7334 | 40.7334 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9575.96 | 1684.02 | 1682.82 | 1723.3123 | 23.68 | 40.4923 | 40.4923 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9595.97 | 1683.17 | 1681.97 | 1723.2811 | 24.53 | 41.3111 | 41.3111 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9616.03 | 1684.65 | 1683.45 | 1723.2498 | 23.05 | 39.7998 | 39.7998 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9636.04 | 1684.11 | 1682.91 | 1723.2187 | 23.59 | 40.3087 | 40.3087 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9656.05 | 1683.53 | 1682.33 | 1723.1875 | 24.17 | 40.8575 | 40.8575 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9676.06 | 1684.18 | 1682.98 | 1723.1563 | 23.52 | 40.1763 | 40.1763 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9696.06 | 1684.36 | 1683.16 | 1723.1252 | 23.34 | 39.9652 | 39.9652 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9716.06 | 1684.81 | 1683.61 | 1723.094 | 22.89 | 39.484 | 39.484 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9736.07 | 1685.36 | 1684.16 | 1723.0629 | 22.34 | 38.9029 | 38.9029 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9756.07 | 1685.47 | 1684.27 | 1723.0317 | 22.23 | 38.7617 | 38.7617 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9776.07 | 1685.72 | 1684.52 | 1723.0005 | 21.98 | 38.4805 | 38.4805 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9796.08 | 1686.13 | 1684.93 | 1722.9694 | 21.57 | 38.0394 | 38.0394 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9816.08 | 1686.17 | 1684.97 | 1722.9382 | 21.53 | 37.9682 | 37.9682 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9836.08 | 1686.07 | 1684.87 | 1722.9071 | 21.63 | 38.0371 | 38.0371 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9856.14 | 1687.71 | 1686.51 | 1722.8758 | 19.99 | 36.3658 | 36.3658 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9876.14 | 1687.75 | 1686.55 | 1722.8447 | 19.95 | 36.2947 | 36.2947 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9896.15 | 1688.23 | 1687.03 | 1722.8135 | 19.47 | 35.7835 | 35.7835 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9916.16 | 1688.81 | 1687.61 | 1722.7823 | 18.89 | 35.1723 | 35.1723 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9936.16 | 1689.05 | 1687.85 | 1722.7512 | 18.65 | 34.9012 | 34.9012 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9956.16 | 1689.43 | 1688.23 | 1722.72 | 18.27 | 34.49 | 34.49 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9976.17 | 1689.93 | 1688.73 | 1722.6889 | 17.77 | 33.9589 | 33.9589 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 9996.17 | 1690.26 | 1689.06 | 1722.6577 | 17.44 | 33.5977 | 33.5977 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10016.18 | 1690.81 | 1689.61 | 1722.6265 | 16.89 | 33.0165 | 33.0165 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10036.18 | 1690.94 | 1689.74 | 1722.5954 | 16.76 | 32.8554 | 32.8554 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10056.19 | 1691.52 | 1690.32 | 1722.5642 | 16.18 | 32.2442 | 32.2442 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10076.19 | 1691.78 | 1690.58 | 1722.5331 | 15.92 | 31.9531 | 31.9531 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10096.19 | 1692.27 | 1691.07 | 1722.5019 | 15.43 | 31.4319 | 31.4319 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10116.21 | 1692.92 | 1691.72 | 1722.4707 | 14.78 | 30.7507 | 30.7507 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10136.21 | 1693.16 | 1691.96 | 1722.4396 | 14.54 | 30.4796 | 30.4796 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10156.21 | 1693.61 | 1692.41 | 1722.4084 | 14.09 | 29.9984 | 29.9984 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10176.23 | 1694.36 | 1693.16 | 1722.3772 | 13.34 | 29.2172 | 29.2172 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10196.23 | 1694.34 | 1693.14 | 1722.3461 | 13.36 | 29.2061 | 29.2061 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10216.23 | 1694.46 | 1693.26 | 1722.3149 | 13.24 | 29.0549 | 29.0549 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10236.23 | 1694.77 | 1693.57 | 1722.2838 | 12.93 | 28.7138 | 28.7138 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10256.23 | 1694.99 | 1693.79 | 1722.2526 | 12.71 | 28.4626 | 28.4626 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10276.24 | 1695.48 | 1694.28 | 1722.2214 | 12.22 | 27.9414 | 27.9414 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10296.24 | 1695.75 | 1694.55 | 1722.1903 | 11.95 | 27.6403 | 27.6403 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10316.24 | 1695.99 | 1694.79 | 1722.1591 | 11.71 | 27.3691 | 27.3691 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10336.24 | 1696.11 | 1694.91 | 1722.128 | 11.59 | 27.218 | 27.218 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10356.24 | 1696.41 | 1695.21 | 1722.0968 | 11.29 | 26.8868 | 26.8868 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10376.24 | 1696.14 | 1694.94 | 1722.0657 | 11.56 | 27.1257 | 27.1257 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10396.24 | 1696.28 | 1695.08 | 1722.0345 | 11.42 | 26.9545 | 26.9545 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10416.24 | 1696.24 | 1695.04 | 1722.0034 | 11.46 | 26.9634 | 26.9634 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10436.25 | 1696.52 | 1695.32 | 1721.9722 | 11.18 | 26.6522 | 26.6522 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10456.25 | 1696.39 | 1695.19 | 1721.9411 | 11.31 | 26.7511 | 26.7511 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10476.25 | 1696.14 | 1694.94 | 1721.9099 | 11.56 | 26.9699 | 26.9699 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10496.25 | 1696.12 | 1694.92 | 1721.8787 | 11.58 | 26.9587 | 26.9587 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10516.25 | 1696.03 | 1694.83 | 1721.8476 | 11.67 | 27.0176 | 27.0176 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10536.25 | 1695.6 | 1694.4 | 1721.8164 | 12.1 | 27.4164 | 27.4164 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10556.25 | 1695.59 | 1694.39 | 1721.7853 | 12.11 | 27.3953 | 27.3953 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10576.28 | 1694.51 | 1693.31 | 1721.7541 | 13.19 | 28.4441 | 28.4441 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10596.28 | 1694.78 | 1693.58 | 1721.7229 | 12.92 | 28.1429 | 28.1429 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10616.29 | 1694.36 | 1693.16 | 1721.6918 | 13.34 | 28.5318 | 28.5318 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10636.29 | 1694.21 | 1693.01 | 1721.6606 | 13.49 | 28.6506 | 28.6506 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10656.3 | 1693.71 | 1692.51 | 1721.6294 | 13.99 | 29.1194 | 29.1194 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10676.3 | 1693.31 | 1692.11 | 1721.5983 | 14.39 | 29.4883 | 29.4883 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10696.3 | 1692.86 | 1691.66 | 1721.5671 | 14.84 | 29.9071 | 29.9071 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10716.31 | 1692.59 | 1691.39 | 1721.536 | 15.11 | 30.146 | 30.146 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10736.32 | 1691.91 | 1690.71 | 1721.5048 | 15.79 | 30.7948 | 30.7948 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10756.32 | 1691.41 | 1690.21 | 1721.4736 | 16.29 | 31.2636 | 31.2636 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10776.33 | 1691.09 | 1689.89 | 1721.4425 | 16.61 | 31.5525 | 31.5525 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10796.35 | 1690.14 | 1688.94 | 1721.4113 | 17.56 | 32.4713 | 32.4713 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10816.35 | 1689.91 | 1688.71 | 1721.3801 | 17.79 | 32.6701 | 32.6701 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10836.36 | 1689.21 | 1688.01 | 1721.349 | 18.49 | 33.339 | 33.339 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10856.36 | 1689 | 1687.8 | 1721.3178 | 18.7 | 33.5178 | 33.5178 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10876.38 | 1688.27 | 1687.07 | 1721.2866 | 19.43 | 34.2166 | 34.2166 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10896.38 | 1688.2 | 1687 | 1721.2555 | 19.5 | 34.2555 | 34.2555 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10916.39 | 1687.54 | 1686.34 | 1721.2243 | 20.16 | 34.8843 | 34.8843 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10936.4 | 1686.96 | 1685.76 | 1721.1931 | 20.74 | 35.4331 | 35.4331 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10956.4 | 1686.92 | 1685.72 | 1721.162 | 20.78 | 35.442 | 35.442 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10976.41 | 1686.31 | 1685.11 | 1721.1308 | 21.39 | 36.0208 | 36.0208 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 10996.41 | 1686.1 | 1684.9 | 1721.0997 | 21.6 | 36.1997 | 36.1997 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11015.91 | 1685.99 | 1684.79 | 1721.0693 | 21.71 | 36.2793 | 36.2793 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11035.91 | 1685.5 | 1684.3 | 1721.0381 | 22.2 | 36.7381 | 36.7381 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11055.91 | 1685.43 | 1684.23 | 1721.007 | 22.27 | 36.777 | 36.777 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11075.91 | 1685.69 | 1684.49 | 1720.9758 | 22.01 | 36.4858 | 36.4858 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11095.92 | 1685.35 | 1684.15 | 1720.9447 | 22.35 | 36.7947 | 36.7947 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11115.92 | 1684.98 | 1683.78 | 1720.9135 | 22.72 | 37.1335 | 37.1335 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11135.92 | 1684.88 | 1683.68 | 1720.8824 | 22.82 | 37.2024 | 37.2024 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11155.92 | 1685.06 | 1683.86 | 1720.8512 | 22.64 | 36.9912 | 36.9912 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11175.93 | 1684.63 | 1683.43 | 1720.82 | 23.07 | 37.39 | 37.39 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11195.93 | 1684.77 | 1683.57 | 1720.7889 | 22.93 | 37.2189 | 37.2189 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11215.93 | 1684.76 | 1683.56 | 1720.7577 | 22.94 | 37.1977 | 37.1977 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11235.85 | 1685.04 | 1683.84 | 1720.7267 | 22.66 | 36.8867 | 36.8867 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11255.85 | 1684.88 | 1683.68 | 1720.6955 | 22.82 | 37.0155 | 37.0155 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11275.85 | 1685.3 | 1684.1 | 1720.6644 | 22.4 | 36.5644 | 36.5644 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11295.86 | 1685.02 | 1683.82 | 1720.6332 | 22.68 | 36.8132 | 36.8132 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11315.86 | 1685.6 | 1684.4 | 1720.6021 | 22.1 | 36.2021 | 36.2021 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11335.86 | 1685.62 | 1684.42 | 1720.5709 | 22.08 | 36.1509 | 36.1509 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11355.87 | 1685.89 | 1684.69 | 1720.5397 | 21.81 | 35.8497 | 35.8497 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11375.87 | 1686.03 | 1684.83 | 1720.5086 | 21.67 | 35.6786 | 35.6786 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11395.87 | 1686.14 | 1684.94 | 1720.4774 | 21.56 | 35.5374 | 35.5374 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11415.87 | 1686.36 | 1685.16 | 1720.4463 | 21.34 | 35.2863 | 35.2863 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11435.87 | 1686.43 | 1685.23 | 1720.4151 | 21.27 | 35.1851 | 35.1851 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11455.89 | 1687.26 | 1686.06 | 1720.3839 | 20.44 | 34.3239 | 34.3239 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11475.89 | 1687.18 | 1685.98 | 1720.3528 | 20.52 | 34.3728 | 34.3728 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11495.89 | 1687.07 | 1685.87 | 1720.3216 | 20.63 | 34.4516 | 34.4516 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11515.89 | 1687.25 | 1686.05 | 1720.2905 | 20.45 | 34.2405 | 34.2405 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11535.89 | 1687.32 | 1686.12 | 1720.2593 | 20.38 | 34.1393 | 34.1393 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11555.89 | 1687.6 | 1686.4 | 1720.2282 | 20.1 | 33.8282 | 33.8282 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11575.89 | 1687.99 | 1686.79 | 1720.197 | 19.71 | 33.407 | 33.407 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11595.89 | 1688.06 | 1686.86 | 1720.1659 | 19.64 | 33.3059 | 33.3059 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11615.89 | 1688.29 | 1687.09 | 1720.1347 | 19.41 | 33.0447 | 33.0447 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11635.9 | 1688.58 | 1687.38 | 1720.1036 | 19.12 | 32.7236 | 32.7236 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11655.91 | 1689.26 | 1688.06 | 1720.0724 | 18.44 | 32.0124 | 32.0124 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11675.91 | 1689.38 | 1688.18 | 1720.0412 | 18.32 | 31.8612 | 31.8612 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11695.91 | 1689.18 | 1687.98 | 1720.0101 | 18.52 | 32.0301 | 32.0301 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11715.91 | 1689.09 | 1687.89 | 1719.9789 | 18.61 | 32.0889 | 32.0889 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11735.92 | 1689.57 | 1688.37 | 1719.9478 | 18.13 | 31.5778 | 31.5778 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11755.92 | 1689.73 | 1688.53 | 1719.9166 | 17.97 | 31.3866 | 31.3866 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11775.92 | 1689.54 | 1688.34 | 1719.8854 | 18.16 | 31.5454 | 31.5454 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11795.92 | 1689.63 | 1688.43 | 1719.8543 | 18.07 | 31.4243 | 31.4243 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11815.92 | 1689.65 | 1688.45 | 1719.8231 | 18.05 | 31.3731 | 31.3731 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11835.92 | 1689.68 | 1688.48 | 1719.792 | 18.02 | 31.312 | 31.312 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11855.92 | 1689.44 | 1688.24 | 1719.7608 | 18.26 | 31.5208 | 31.5208 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11875.92 | 1689.14 | 1687.94 | 1719.7297 | 18.56 | 31.7897 | 31.7897 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11895.92 | 1689.08 | 1687.88 | 1719.6985 | 18.62 | 31.8185 | 31.8185 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11915.93 | 1688.44 | 1687.24 | 1719.6674 | 19.26 | 32.4274 | 32.4274 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11935.93 | 1688.44 | 1687.24 | 1719.6362 | 19.26 | 32.3962 | 32.3962 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11955.93 | 1688.23 | 1687.03 | 1719.6051 | 19.47 | 32.5751 | 32.5751 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11975.94 | 1687.66 | 1686.46 | 1719.5739 | 20.04 | 33.1139 | 33.1139 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 11995.85 | 1688.15 | 1686.95 | 1719.5429 | 19.55 | 32.5929 | 32.5929 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12015.86 | 1687.43 | 1686.23 | 1719.5117 | 20.27 | 33.2817 | 33.2817 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12035.86 | 1687.43 | 1686.23 | 1719.4805 | 20.27 | 33.2505 | 33.2505 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12055.86 | 1686.98 | 1685.78 | 1719.4494 | 20.72 | 33.6694 | 33.6694 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12075.86 | 1686.98 | 1685.78 | 1719.4182 | 20.72 | 33.6382 | 33.6382 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12095.88 | 1686.25 | 1685.05 | 1719.3871 | 21.45 | 34.3371 | 34.3371 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12115.88 | 1686.03 | 1684.83 | 1719.3559 | 21.67 | 34.5259 | 34.5259 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12135.91 | 1684.88 | 1683.68 | 1719.3247 | 22.82 | 35.6447 | 35.6447 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12155.92 | 1684.47 | 1683.27 | 1719.2935 | 23.23 | 36.0235 | 36.0235 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12175.92 | 1684.82 | 1683.62 | 1719.2624 | 22.88 | 35.6424 | 35.6424 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12195.99 | 1683.14 | 1681.94 | 1719.2311 | 24.56 | 37.2911 | 37.2911 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12216.02 | 1682.05 | 1680.85 | 1719.1999 | 25.65 | 38.3499 | 38.3499 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12236.02 | 1681.7 | 1680.5 | 1719.1688 | 26 | 38.6688 | 38.6688 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12256.05 | 1680.6 | 1679.4 | 1719.1376 | 27.1 | 39.7376 | 39.7376 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12276.07 | 1679.66 | 1678.46 | 1719.1064 | 28.04 | 40.6464 | 40.6464 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12296.13 | 1678.14 | 1676.94 | 1719.0751 | 29.56 | 42.1351 | 42.1351 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12316.14 | 1677.57 | 1676.37 | 1719.044 | 30.13 | 42.674 | 42.674 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12336.28 | 1675.18 | 1673.98 | 1719.0126 | 32.52 | 45.0326 | 45.0326 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12356.28 | 1675.18 | 1673.98 | 1718.9814 | 32.52 | 45.0014 | 45.0014 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12376.68 | 1671.17 | 1669.97 | 1718.9497 | 36.53 | 48.9797 | 48.9797 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12396.68 | 1670.96 | 1669.76 | 1718.9185 | 36.74 | 49.1585 | 49.1585 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12417 | 1667.4 | 1666.2 | 1718.8869 | 40.3 | 52.6869 | 52.6869 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12437 | 1667.46 | 1666.26 | 1718.8557 | 40.24 | 52.5957 | 52.5957 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12457 | 1667.46 | 1666.26 | 1718.8246 | 40.24 | 52.5646 | 52.5646 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12477.68 | 1662.2 | 1661 | 1718.7923 | 45.5 | 57.7923 | 57.7923 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12497.68 | 1662.21 | 1661.01 | 1718.7612 | 45.49 | 57.7512 | 57.7512 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12517.69 | 1661.87 | 1660.67 | 1718.73 | 45.83 | 58.06 | 58.06 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12537.71 | 1661.06 | 1659.86 | 1718.6988 | 46.64 | 58.8388 | 58.8388 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12557.71 | 1661.06 | 1659.86 | 1718.6677 | 46.64 | 58.8077 | 58.8077 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12577.71 | 1660.56 | 1659.36 | 1718.6365 | 47.14 | 59.2765 | 59.2765 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12597.74 | 1659.5 | 1658.3 | 1718.6053 | 48.2 | 60.3053 | 60.3053 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12617.74 | 1659.5 | 1658.3 | 1718.5742 | 48.2 | 60.2742 | 60.2742 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12637.74 | 1659.27 | 1658.07 | 1718.543 | 48.43 | 60.473 | 60.473 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12657.83 | 1657.44 | 1656.24 | 1718.5117 | 50.26 | 62.2717 | 62.2717 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12677.84 | 1658.29 | 1657.09 | 1718.4806 | 49.41 | 61.3906 | 61.3906 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12697.89 | 1656.91 | 1655.71 | 1718.4493 | 50.79 | 62.7393 | 62.7393 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12718.02 | 1654.66 | 1653.46 | 1718.418 | 53.04 | 64.958 | 64.958 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12738.05 | 1653.47 | 1652.27 | 1718.3868 | 54.23 | 66.1168 | 66.1168 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12758.28 | 1651.68 | 1650.48 | 1718.3553 | 56.02 | 67.8753 | 67.8753 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12778.34 | 1650.15 | 1648.95 | 1718.324 | 57.55 | 69.374 | 69.374 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12798.38 | 1651.45 | 1650.25 | 1718.2928 | 56.25 | 68.0428 | 68.0428 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12818.45 | 1653.14 | 1651.94 | 1718.2615 | 54.56 | 66.3215 | 66.3215 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12838.61 | 1655.62 | 1654.42 | 1718.2301 | 52.08 | 63.8101 | 63.8101 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12858.61 | 1655.67 | 1654.47 | 1718.199 | 52.03 | 63.729 | 63.729 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12878.84 | 1658.74 | 1657.54 | 1718.1675 | 48.96 | 60.6275 | 60.6275 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12898.85 | 1659.36 | 1658.16 | 1718.1363 | 48.34 | 59.9763 | 59.9763 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12918.91 | 1660.96 | 1659.76 | 1718.1051 | 46.74 | 58.3451 | 58.3451 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12939.1 | 1663.7 | 1662.5 | 1718.0736 | 44 | 55.5736 | 55.5736 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12959.14 | 1662.54 | 1661.34 | 1718.0424 | 45.16 | 56.7024 | 56.7024 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12979.15 | 1661.84 | 1660.64 | 1718.0112 | 45.86 | 57.3712 | 57.3712 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 12999.15 | 1661.56 | 1660.36 | 1717.9801 | 46.14 | 57.6201 | 57.6201 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13019.15 | 1662.03 | 1660.83 | 1717.9489 | 45.67 | 57.1189 | 57.1189 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13039.17 | 1661.38 | 1660.18 | 1717.9177 | 46.32 | 57.7377 | 57.7377 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13059.19 | 1660.38 | 1659.18 | 1717.8865 | 47.32 | 58.7065 | 58.7065 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13079.3 | 1662.44 | 1661.24 | 1717.8552 | 45.26 | 56.6152 | 56.6152 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13099.44 | 1660.06 | 1658.86 | 1717.8238 | 47.64 | 58.9638 | 58.9638 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13118.99 | 1661.23 | 1660.03 | 1717.7934 | 46.47 | 57.7634 | 57.7634 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13139.07 | 1659.51 | 1658.31 | 1717.7621 | 48.19 | 59.4521 | 59.4521 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13159.17 | 1657.44 | 1656.24 | 1717.7308 | 50.26 | 61.4908 | 61.4908 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13179.18 | 1657.01 | 1655.81 | 1717.6996 | 50.69 | 61.8896 | 61.8896 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13199.64 | 1652.67 | 1651.47 | 1717.6678 | 55.03 | 66.1978 | 66.1978 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13219.88 | 1655.73 | 1654.53 | 1717.6362 | 51.97 | 63.1062 | 63.1062 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13240.66 | 1660.65 | 1659.45 | 1717.6039 | 47.05 | 58.1539 | 58.1539 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13260.87 | 1663.55 | 1662.35 | 1717.5724 | 44.15 | 55.2224 | 55.2224 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13280.97 | 1665.55 | 1664.35 | 1717.5411 | 42.15 | 53.1911 | 53.1911 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13301.21 | 1668.71 | 1667.51 | 1717.5096 | 38.99 | 49.9996 | 49.9996 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13321.22 | 1669.18 | 1667.98 | 1717.4784 | 38.52 | 49.4984 | 49.4984 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13341.63 | 1673.28 | 1672.08 | 1717.4466 | 34.42 | 45.3666 | 45.3666 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13361.79 | 1675.74 | 1674.54 | 1717.4152 | 31.96 | 42.8752 | 42.8752 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13381.97 | 1678.47 | 1677.27 | 1717.3838 | 29.23 | 40.1138 | 40.1138 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13401.97 | 1678.47 | 1677.27 | 1717.3526 | 29.23 | 40.0826 | 40.0826 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13422.48 | 1683.03 | 1681.83 | 1717.3207 | 24.67 | 35.4907 | 35.4907 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13442.62 | 1685.35 | 1684.15 | 1717.2893 | 22.35 | 33.1393 | 33.1393 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13462.79 | 1685.94 | 1684.74 | 1717.2579 | 21.76 | 32.5179 | 32.5179 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13482.88 | 1687.86 | 1686.66 | 1717.2266 | 19.84 | 30.5666 | 30.5666 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13502.97 | 1689.81 | 1688.61 | 1717.1953 | 17.89 | 28.5853 | 28.5853 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13523.11 | 1692.14 | 1690.94 | 1717.1639 | 15.56 | 26.2239 | 26.2239 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13543.12 | 1692.79 | 1691.59 | 1717.1327 | 14.91 | 25.5427 | 25.5427 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13562.72 | 1692.77 | 1691.57 | 1717.1022 | 14.93 | 25.5322 | 25.5322 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13582.73 | 1693.23 | 1692.03 | 1717.071 | 14.47 | 25.041 | 25.041 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13602.74 | 1694.06 | 1692.86 | 1717.0399 | 13.64 | 24.1799 | 24.1799 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13622.74 | 1694.38 | 1693.18 | 1717.0087 | 13.32 | 23.8287 | 23.8287 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13642.74 | 1694.41 | 1693.21 | 1716.9776 | 13.29 | 23.7676 | 23.7676 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13662.74 | 1694.37 | 1693.17 | 1716.9464 | 13.33 | 23.7764 | 23.7764 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13682.75 | 1694.84 | 1693.64 | 1716.9152 | 12.86 | 23.2752 | 23.2752 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13702.58 | 1694.93 | 1693.73 | 1716.8844 | 12.77 | 23.1544 | 23.1544 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13722.58 | 1694.93 | 1693.73 | 1716.8532 | 12.77 | 23.1232 | 23.1232 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13742.58 | 1694.61 | 1693.41 | 1716.8221 | 13.09 | 23.4121 | 23.4121 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13762.59 | 1694.97 | 1693.77 | 1716.7909 | 12.73 | 23.0209 | 23.0209 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13782.59 | 1694.64 | 1693.44 | 1716.7597 | 13.06 | 23.3197 | 23.3197 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13802.6 | 1695.28 | 1694.08 | 1716.7286 | 12.42 | 22.6486 | 22.6486 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13822.6 | 1695.27 | 1694.07 | 1716.6974 | 12.43 | 22.6274 | 22.6274 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13842.6 | 1695.37 | 1694.17 | 1716.6663 | 12.33 | 22.4963 | 22.4963 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13862.6 | 1695.5 | 1694.3 | 1716.6351 | 12.2 | 22.3351 | 22.3351 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13882.6 | 1695.35 | 1694.15 | 1716.6039 | 12.35 | 22.4539 | 22.4539 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13902.6 | 1695.75 | 1694.55 | 1716.5728 | 11.95 | 22.0228 | 22.0228 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13922.6 | 1695.79 | 1694.59 | 1716.5416 | 11.91 | 21.9516 | 21.9516 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13942.6 | 1695.89 | 1694.69 | 1716.5105 | 11.81 | 21.8205 | 21.8205 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13962.61 | 1696.23 | 1695.03 | 1716.4793 | 11.47 | 21.4493 | 21.4493 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 13982.54 | 1696.92 | 1695.72 | 1716.4483 | 10.78 | 20.7283 | 20.7283 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14002.54 | 1697.27 | 1696.07 | 1716.4171 | 10.43 | 20.3471 | 20.3471 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14022.54 | 1697.27 | 1696.07 | 1716.386 | 10.43 | 20.316 | 20.316 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14042.54 | 1697.54 | 1696.34 | 1716.3548 | 10.16 | 20.0148 | 20.0148 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14062.55 | 1697.72 | 1696.52 | 1716.3236 | 9.98 | 19.8036 | 19.8036 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14082.57 | 1698.74 | 1697.54 | 1716.2925 | 8.96 | 18.7525 | 18.7525 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14102.57 | 1698.68 | 1697.48 | 1716.2613 | 9.02 | 18.7813 | 18.7813 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14122.57 | 1698.93 | 1697.73 | 1716.2302 | 8.77 | 18.5002 | 18.5002 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14142.45 | 1699.58 | 1698.38 | 1716.1992 | 8.12 | 17.8192 | 17.8192 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14162.46 | 1699.85 | 1698.65 | 1716.168 | 7.85 | 17.518 | 17.518 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14182.46 | 1700.43 | 1699.23 | 1716.1369 | 7.27 | 16.9069 | 16.9069 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14202.48 | 1701.31 | 1700.11 | 1716.1057 | 6.39 | 15.9957 | 15.9957 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14222.65 | 1701.53 | 1700.33 | 1716.0743 | 6.17 | 15.7443 | 15.7443 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14242.66 | 1701.72 | 1700.52 | 1716.0431 | 5.98 | 15.5231 | 15.5231 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14262.66 | 1702.03 | 1700.83 | 1716.0119 | 5.67 | 15.1819 | 15.1819 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14282.66 | 1702.18 | 1700.98 | 1715.9808 | 5.52 | 15.0008 | 15.0008 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14302.66 | 1702.18 | 1700.98 | 1715.9496 | 5.52 | 14.9696 | 14.9696 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14322.7 | 1703.5 | 1702.3 | 1715.9184 | 4.2 | 13.6184 | 13.6184 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14342.63 | 1704.1 | 1702.9 | 1715.8874 | 3.6 | 12.9874 | 12.9874 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14362.63 | 1704.22 | 1703.02 | 1715.8562 | 3.48 | 12.8362 | 12.8362 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14382.63 | 1704.55 | 1703.35 | 1715.8251 | 3.15 | 12.4751 | 12.4751 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14402.66 | 1705.63 | 1704.43 | 1715.7939 | 2.07 | 11.3639 | 11.3639 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14422.72 | 1706.68 | 1705.48 | 1715.7626 | 1.02 | 10.2826 | 10.2826 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14442.74 | 1707.58 | 1706.38 | 1715.7314 | 0.12 | 9.3514 | 9.3514 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14462.76 | 1708.45 | 1707.25 | 1715.7003 | -0.75 | 8.4503 | 8.4503 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14482.76 | 1708.64 | 1707.44 | 1715.6691 | -0.94 | 8.2291 | 8.2291 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14502.77 | 1709.18 | 1707.98 | 1715.6379 | -1.48 | 7.6579 | 7.6579 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14522.92 | 1709.55 | 1708.35 | 1715.6065 | -1.85 | 7.2565 | 7.2565 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14542.92 | 1709.77 | 1708.57 | 1715.5754 | -2.07 | 7.0054 | 7.0054 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14563.14 | 1709.96 | 1708.76 | 1715.5439 | -2.26 | 6.7839 | 6.7839 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14583.14 | 1710.04 | 1708.84 | 1715.5127 | -2.34 | 6.6727 | 6.6727 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14603.14 | 1709.86 | 1708.66 | 1715.4816 | -2.16 | 6.8216 | 6.8216 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14623.38 | 1709.06 | 1707.86 | 1715.4501 | -1.36 | 7.5901 | 7.5901 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14643.4 | 1708.07 | 1706.87 | 1715.4189 | -0.37 | 8.5489 | 8.5489 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14663.4 | 1708.02 | 1706.82 | 1715.3877 | -0.32 | 8.5677 | 8.5677 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14683.45 | 1706.72 | 1705.52 | 1715.3565 | 0.98 | 9.8365 | 9.8365 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14703.45 | 1706.81 | 1705.61 | 1715.3253 | 0.89 | 9.7153 | 9.7153 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14723.49 | 1705.58 | 1704.38 | 1715.2941 | 2.12 | 10.9141 | 10.9141 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14743.49 | 1705.58 | 1704.38 | 1715.263 | 2.12 | 10.883 | 10.883 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14763.43 | 1705.06 | 1703.86 | 1715.2319 | 2.64 | 11.3719 | 11.3719 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14783.45 | 1704.12 | 1702.92 | 1715.2007 | 3.58 | 12.2807 | 12.2807 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14803.46 | 1703.83 | 1702.63 | 1715.1696 | 3.87 | 12.5396 | 12.5396 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14823.49 | 1702.64 | 1701.44 | 1715.1384 | 5.06 | 13.6984 | 13.6984 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14843.49 | 1702.39 | 1701.19 | 1715.1072 | 5.31 | 13.9172 | 13.9172 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14863.51 | 1701.53 | 1700.33 | 1715.076 | 6.17 | 14.746 | 14.746 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14883.52 | 1700.91 | 1699.71 | 1715.0448 | 6.79 | 15.3348 | 15.3348 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14903.53 | 1700.39 | 1699.19 | 1715.0137 | 7.31 | 15.8237 | 15.8237 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14923.54 | 1699.82 | 1698.62 | 1714.9825 | 7.88 | 16.3625 | 16.3625 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14943.55 | 1699.12 | 1697.92 | 1714.9513 | 8.58 | 17.0313 | 17.0313 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14963.56 | 1698.48 | 1697.28 | 1714.9202 | 9.22 | 17.6402 | 17.6402 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 14983.57 | 1697.91 | 1696.71 | 1714.889 | 9.79 | 18.179 | 18.179 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15003.57 | 1697.74 | 1696.54 | 1714.8579 | 9.96 | 18.3179 | 18.3179 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15023.58 | 1696.94 | 1695.74 | 1714.8267 | 10.76 | 19.0867 | 19.0867 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15043.59 | 1696.44 | 1695.24 | 1714.7955 | 11.26 | 19.5555 | 19.5555 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15063.59 | 1696.02 | 1694.82 | 1714.7644 | 11.68 | 19.9444 | 19.9444 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15083.6 | 1695.72 | 1694.52 | 1714.7332 | 11.98 | 20.2132 | 20.2132 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15103.6 | 1696.06 | 1694.86 | 1714.702 | 11.64 | 19.842 | 19.842 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15123.6 | 1696.06 | 1694.86 | 1714.6709 | 11.64 | 19.8109 | 19.8109 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15143.67 | 1694.33 | 1693.13 | 1714.6396 | 13.37 | 21.5096 | 21.5096 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15163.68 | 1693.96 | 1692.76 | 1714.6085 | 13.74 | 21.8485 | 21.8485 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15183.68 | 1693.43 | 1692.23 | 1714.5773 | 14.27 | 22.3473 | 22.3473 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15203.76 | 1693.09 | 1691.89 | 1714.546 | 14.61 | 22.656 | 22.656 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15223.76 | 1693.09 | 1691.89 | 1714.5149 | 14.61 | 22.6249 | 22.6249 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15243.76 | 1692.76 | 1691.56 | 1714.4837 | 14.94 | 22.9237 | 22.9237 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15263.76 | 1692.62 | 1691.42 | 1714.4526 | 15.08 | 23.0326 | 23.0326 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15283.76 | 1692.32 | 1691.12 | 1714.4214 | 15.38 | 23.3014 | 23.3014 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15303.76 | 1692.52 | 1691.32 | 1714.3903 | 15.18 | 23.0703 | 23.0703 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15323.78 | 1691.63 | 1690.43 | 1714.3591 | 16.07 | 23.9291 | 23.9291 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15343.81 | 1692.67 | 1691.47 | 1714.3279 | 15.03 | 22.8579 | 22.8579 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15363.83 | 1691.84 | 1690.64 | 1714.2967 | 15.86 | 23.6567 | 23.6567 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15383.83 | 1691.41 | 1690.21 | 1714.2655 | 16.29 | 24.0555 | 24.0555 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15403.79 | 1691.39 | 1690.19 | 1714.2344 | 16.31 | 24.0444 | 24.0444 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15423.79 | 1691.19 | 1689.99 | 1714.2033 | 16.51 | 24.2133 | 24.2133 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15443.8 | 1690.67 | 1689.47 | 1714.1721 | 17.03 | 24.7021 | 24.7021 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15463.8 | 1690.75 | 1689.55 | 1714.141 | 16.95 | 24.591 | 24.591 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15483.8 | 1690.72 | 1689.52 | 1714.1098 | 16.98 | 24.5898 | 24.5898 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15503.8 | 1690.5 | 1689.3 | 1714.0787 | 17.2 | 24.7787 | 24.7787 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15523.8 | 1690.5 | 1689.3 | 1714.0475 | 17.2 | 24.7475 | 24.7475 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15543.8 | 1690.35 | 1689.15 | 1714.0164 | 17.35 | 24.8664 | 24.8664 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15563.8 | 1690.45 | 1689.25 | 1713.9852 | 17.25 | 24.7352 | 24.7352 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15583.8 | 1690.4 | 1689.2 | 1713.954 | 17.3 | 24.754 | 24.754 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15603.8 | 1690.26 | 1689.06 | 1713.9229 | 17.44 | 24.8629 | 24.8629 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15623.82 | 1689.45 | 1688.25 | 1713.8917 | 18.25 | 25.6417 | 25.6417 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15643.82 | 1689.45 | 1688.25 | 1713.8606 | 18.25 | 25.6106 | 25.6106 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15663.82 | 1688.98 | 1687.78 | 1713.8294 | 18.72 | 26.0494 | 26.0494 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15683.82 | 1688.98 | 1687.78 | 1713.7982 | 18.72 | 26.0182 | 26.0182 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15703.82 | 1688.94 | 1687.74 | 1713.7671 | 18.76 | 26.0271 | 26.0271 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15723.83 | 1688.68 | 1687.48 | 1713.7359 | 19.02 | 26.2559 | 26.2559 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15743.84 | 1688.02 | 1686.82 | 1713.7048 | 19.68 | 26.8848 | 26.8848 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15763.84 | 1687.62 | 1686.42 | 1713.6736 | 20.08 | 27.2536 | 27.2536 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15783.84 | 1687.7 | 1686.5 | 1713.6425 | 20 | 27.1425 | 27.1425 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15803.84 | 1687.44 | 1686.24 | 1713.6113 | 20.26 | 27.3713 | 27.3713 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15823.84 | 1687.44 | 1686.24 | 1713.5801 | 20.26 | 27.3401 | 27.3401 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15843.85 | 1686.79 | 1685.59 | 1713.549 | 20.91 | 27.959 | 27.959 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15863.85 | 1686.79 | 1685.59 | 1713.5178 | 20.91 | 27.9278 | 27.9278 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15883.86 | 1686.24 | 1685.04 | 1713.4867 | 21.46 | 28.4467 | 28.4467 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15903.86 | 1686.24 | 1685.04 | 1713.4555 | 21.46 | 28.4155 | 28.4155 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15923.87 | 1685.57 | 1684.37 | 1713.4243 | 22.13 | 29.0543 | 29.0543 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15943.87 | 1685.57 | 1684.37 | 1713.3932 | 22.13 | 29.0232 | 29.0232 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15963.87 | 1685.4 | 1684.2 | 1713.362 | 22.3 | 29.162 | 29.162 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 15983.87 | 1685.4 | 1684.2 | 1713.3309 | 22.3 | 29.1309 | 29.1309 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16003.88 | 1684.75 | 1683.55 | 1713.2997 | 22.95 | 29.7497 | 29.7497 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16023.88 | 1684.75 | 1683.55 | 1713.2685 | 22.95 | 29.7185 | 29.7185 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16043.88 | 1684.58 | 1683.38 | 1713.2374 | 23.12 | 29.8574 | 29.8574 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16063.89 | 1684.36 | 1683.16 | 1713.2062 | 23.34 | 30.0462 | 30.0462 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16083.89 | 1684 | 1682.8 | 1713.1751 | 23.7 | 30.3751 | 30.3751 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16103.89 | 1683.96 | 1682.76 | 1713.1439 | 23.74 | 30.3839 | 30.3839 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16123.89 | 1683.63 | 1682.43 | 1713.1128 | 24.07 | 30.6828 | 30.6828 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16143.89 | 1683.54 | 1682.34 | 1713.0816 | 24.16 | 30.7416 | 30.7416 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16163.9 | 1683.97 | 1682.77 | 1713.0504 | 23.73 | 30.2804 | 30.2804 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16183.9 | 1683.53 | 1682.33 | 1713.0193 | 24.17 | 30.6893 | 30.6893 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16203.9 | 1683.34 | 1682.14 | 1712.9881 | 24.36 | 30.8481 | 30.8481 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16223.9 | 1683.16 | 1681.96 | 1712.957 | 24.54 | 30.997 | 30.997 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16243.91 | 1682.58 | 1681.38 | 1712.9258 | 25.12 | 31.5458 | 31.5458 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16263.91 | 1682.58 | 1681.38 | 1712.8947 | 25.12 | 31.5147 | 31.5147 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16283.91 | 1682.47 | 1681.27 | 1712.8635 | 25.23 | 31.5935 | 31.5935 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16303.89 | 1682.4 | 1681.2 | 1712.8324 | 25.3 | 31.6324 | 31.6324 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16323.89 | 1682.17 | 1680.97 | 1712.8012 | 25.53 | 31.8312 | 31.8312 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16343.89 | 1682.09 | 1680.89 | 1712.7701 | 25.61 | 31.8801 | 31.8801 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16363.89 | 1682.11 | 1680.91 | 1712.7389 | 25.59 | 31.8289 | 31.8289 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16383.9 | 1681.65 | 1680.45 | 1712.7078 | 26.05 | 32.2578 | 32.2578 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16403.9 | 1681.65 | 1680.45 | 1712.6766 | 26.05 | 32.2266 | 32.2266 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16423.9 | 1681.79 | 1680.59 | 1712.6455 | 25.91 | 32.0555 | 32.0555 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16443.9 | 1681.69 | 1680.49 | 1712.6143 | 26.01 | 32.1243 | 32.1243 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16463.9 | 1681.69 | 1680.49 | 1712.5831 | 26.01 | 32.0931 | 32.0931 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16483.91 | 1682.26 | 1681.06 | 1712.552 | 25.44 | 31.492 | 31.492 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16503.91 | 1682.51 | 1681.31 | 1712.5208 | 25.19 | 31.2108 | 31.2108 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16523.91 | 1682.71 | 1681.51 | 1712.4897 | 24.99 | 30.9797 | 30.9797 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16543.91 | 1682.99 | 1681.79 | 1712.4585 | 24.71 | 30.6685 | 30.6685 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16563.91 | 1682.99 | 1681.79 | 1712.4274 | 24.71 | 30.6374 | 30.6374 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16584.01 | 1685.01 | 1683.81 | 1712.3961 | 22.69 | 28.5861 | 28.5861 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16604.02 | 1685.41 | 1684.21 | 1712.3649 | 22.29 | 28.1549 | 28.1549 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16624.07 | 1686.79 | 1685.59 | 1712.3337 | 20.91 | 26.7437 | 26.7437 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16644.07 | 1686.31 | 1685.11 | 1712.3025 | 21.39 | 27.1925 | 27.1925 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16664.1 | 1687.39 | 1686.19 | 1712.2713 | 20.31 | 26.0813 | 26.0813 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16684.1 | 1687.76 | 1686.56 | 1712.2401 | 19.94 | 25.6801 | 25.6801 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16704.11 | 1688.36 | 1687.16 | 1712.209 | 19.34 | 25.049 | 25.049 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16724.12 | 1689.02 | 1687.82 | 1712.1778 | 18.68 | 24.3578 | 24.3578 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16744.12 | 1689.07 | 1687.87 | 1712.1467 | 18.63 | 24.2767 | 24.2767 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16764.13 | 1689.55 | 1688.35 | 1712.1155 | 18.15 | 23.7655 | 23.7655 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16784.13 | 1689.55 | 1688.35 | 1712.0843 | 18.15 | 23.7343 | 23.7343 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16804.22 | 1691.43 | 1690.23 | 1712.053 | 16.27 | 21.823 | 21.823 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16824.22 | 1691.87 | 1690.67 | 1712.0219 | 15.83 | 21.3519 | 21.3519 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16844.25 | 1693.27 | 1692.07 | 1711.9907 | 14.43 | 19.9207 | 19.9207 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16864.27 | 1694.07 | 1692.87 | 1711.9595 | 13.63 | 19.0895 | 19.0895 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16884.27 | 1694.48 | 1693.28 | 1711.9284 | 13.22 | 18.6484 | 18.6484 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16904.3 | 1695.48 | 1694.28 | 1711.8972 | 12.22 | 17.6172 | 17.6172 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16924.41 | 1695.9 | 1694.7 | 1711.8658 | 11.8 | 17.1658 | 17.1658 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16944.41 | 1696 | 1694.8 | 1711.8347 | 11.7 | 17.0347 | 17.0347 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16964.43 | 1696.93 | 1695.73 | 1711.8035 | 10.77 | 16.0735 | 16.0735 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 16984.57 | 1696.58 | 1695.38 | 1711.7721 | 11.12 | 16.3921 | 16.3921 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17004.59 | 1697.53 | 1696.33 | 1711.7409 | 10.17 | 15.4109 | 15.4109 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17024.59 | 1698.01 | 1696.81 | 1711.7098 | 9.69 | 14.8998 | 14.8998 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17044.6 | 1697.72 | 1696.52 | 1711.6786 | 9.98 | 15.1586 | 15.1586 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17064.6 | 1698.25 | 1697.05 | 1711.6475 | 9.45 | 14.5975 | 14.5975 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17084.6 | 1698.23 | 1697.03 | 1711.6163 | 9.47 | 14.5863 | 14.5863 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17104.6 | 1698.1 | 1696.9 | 1711.5852 | 9.6 | 14.6852 | 14.6852 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17124.6 | 1698.18 | 1696.98 | 1711.554 | 9.52 | 14.574 | 14.574 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17144.6 | 1698.18 | 1696.98 | 1711.5228 | 9.52 | 14.5428 | 14.5428 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17164.61 | 1697.55 | 1696.35 | 1711.4917 | 10.15 | 15.1417 | 15.1417 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17184.63 | 1698.27 | 1697.07 | 1711.4605 | 9.43 | 14.3905 | 14.3905 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17204.68 | 1696.77 | 1695.57 | 1711.4293 | 10.93 | 15.8593 | 15.8593 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17224.68 | 1696.71 | 1695.51 | 1711.3981 | 10.99 | 15.8881 | 15.8881 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17244.71 | 1695.62 | 1694.42 | 1711.3669 | 12.08 | 16.9469 | 16.9469 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17264.71 | 1695.62 | 1694.42 | 1711.3358 | 12.08 | 16.9158 | 16.9158 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17284.71 | 1695.37 | 1694.17 | 1711.3046 | 12.33 | 17.1346 | 17.1346 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17304.73 | 1694.62 | 1693.42 | 1711.2734 | 13.08 | 17.8534 | 17.8534 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17324.73 | 1694.89 | 1693.69 | 1711.2423 | 12.81 | 17.5523 | 17.5523 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17344.73 | 1694.74 | 1693.54 | 1711.2111 | 12.96 | 17.6711 | 17.6711 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17364.82 | 1695.09 | 1693.89 | 1711.1798 | 12.61 | 17.2898 | 17.2898 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17384.82 | 1695.09 | 1693.89 | 1711.1487 | 12.61 | 17.2587 | 17.2587 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17404.82 | 1694.99 | 1693.79 | 1711.1175 | 12.71 | 17.3275 | 17.3275 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17424.83 | 1695.2 | 1694 | 1711.0863 | 12.5 | 17.0863 | 17.0863 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17444.83 | 1695.68 | 1694.48 | 1711.0552 | 12.02 | 16.5752 | 16.5752 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17464.83 | 1695.6 | 1694.4 | 1711.024 | 12.1 | 16.624 | 16.624 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17484.83 | 1695.51 | 1694.31 | 1710.9929 | 12.19 | 16.6829 | 16.6829 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17504.83 | 1695.89 | 1694.69 | 1710.9617 | 11.81 | 16.2717 | 16.2717 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17524.84 | 1695.7 | 1694.5 | 1710.9306 | 12 | 16.4306 | 16.4306 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17544.84 | 1695.59 | 1694.39 | 1710.8994 | 12.11 | 16.5094 | 16.5094 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17564.84 | 1695.77 | 1694.57 | 1710.8683 | 11.93 | 16.2983 | 16.2983 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17584.84 | 1695.67 | 1694.47 | 1710.8371 | 12.03 | 16.3671 | 16.3671 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17604.84 | 1695.97 | 1694.77 | 1710.8059 | 11.73 | 16.0359 | 16.0359 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17624.84 | 1696.3 | 1695.1 | 1710.7748 | 11.4 | 15.6748 | 15.6748 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17644.84 | 1696.01 | 1694.81 | 1710.7436 | 11.69 | 15.9336 | 15.9336 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17664.85 | 1696.3 | 1695.1 | 1710.7125 | 11.4 | 15.6125 | 15.6125 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17684.85 | 1696.06 | 1694.86 | 1710.6813 | 11.64 | 15.8213 | 15.8213 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17704.85 | 1695.92 | 1694.72 | 1710.6502 | 11.78 | 15.9302 | 15.9302 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17724.85 | 1695.95 | 1694.75 | 1710.619 | 11.75 | 15.869 | 15.869 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17744.85 | 1695.95 | 1694.75 | 1710.5879 | 11.75 | 15.8379 | 15.8379 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17764.86 | 1695.8 | 1694.6 | 1710.5567 | 11.9 | 15.9567 | 15.9567 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17784.87 | 1696.37 | 1695.17 | 1710.5255 | 11.33 | 15.3555 | 15.3555 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17804.88 | 1695.56 | 1694.36 | 1710.4943 | 12.14 | 16.1343 | 16.1343 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17824.88 | 1695.53 | 1694.33 | 1710.4632 | 12.17 | 16.1332 | 16.1332 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17844.88 | 1695.53 | 1694.33 | 1710.432 | 12.17 | 16.102 | 16.102 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17864.89 | 1696.2 | 1695 | 1710.4009 | 11.5 | 15.4009 | 15.4009 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17884.89 | 1696.15 | 1694.95 | 1710.3697 | 11.55 | 15.4197 | 15.4197 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17904.94 | 1694.85 | 1693.65 | 1710.3385 | 12.85 | 16.6885 | 16.6885 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17925.13 | 1695.33 | 1694.13 | 1710.307 | 12.37 | 16.177 | 16.177 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17945.14 | 1695.95 | 1694.75 | 1710.2759 | 11.75 | 15.5259 | 15.5259 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17965.15 | 1696.58 | 1695.38 | 1710.2447 | 11.12 | 14.8647 | 14.8647 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 17985.15 | 1696.64 | 1695.44 | 1710.2135 | 11.06 | 14.7735 | 14.7735 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18005.16 | 1696.02 | 1694.82 | 1710.1824 | 11.68 | 15.3624 | 15.3624 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18025.16 | 1696.02 | 1694.82 | 1710.1512 | 11.68 | 15.3312 | 15.3312 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18045.57 | 1696.09 | 1694.89 | 1710.1194 | 11.61 | 15.2294 | 15.2294 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18065.58 | 1696.72 | 1695.52 | 1710.0883 | 10.98 | 14.5683 | 14.5683 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18085.59 | 1696.01 | 1694.81 | 1710.0571 | 11.69 | 15.2471 | 15.2471 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18105.61 | 1696.82 | 1695.62 | 1710.0259 | 10.88 | 14.4059 | 14.4059 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18125.61 | 1697.08 | 1695.88 | 1709.9948 | 10.62 | 14.1148 | 14.1148 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18145.61 | 1697.02 | 1695.82 | 1709.9636 | 10.68 | 14.1436 | 14.1436 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18165.61 | 1697.17 | 1695.97 | 1709.9325 | 10.53 | 13.9625 | 13.9625 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18185.62 | 1697.46 | 1696.26 | 1709.9013 | 10.24 | 13.6413 | 13.6413 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18205.62 | 1697.21 | 1696.01 | 1709.8701 | 10.49 | 13.8601 | 13.8601 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18225.62 | 1697.75 | 1696.55 | 1709.839 | 9.95 | 13.289 | 13.289 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18245.63 | 1697.38 | 1696.18 | 1709.8078 | 10.32 | 13.6278 | 13.6278 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18265.63 | 1697.69 | 1696.49 | 1709.7767 | 10.01 | 13.2867 | 13.2867 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18285.63 | 1697.79 | 1696.59 | 1709.7455 | 9.91 | 13.1555 | 13.1555 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18305.63 | 1697.81 | 1696.61 | 1709.7143 | 9.89 | 13.1043 | 13.1043 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18325.63 | 1697.8 | 1696.6 | 1709.6832 | 9.9 | 13.0832 | 13.0832 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18345.63 | 1697.62 | 1696.42 | 1709.652 | 10.08 | 13.232 | 13.232 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18365.63 | 1697.62 | 1696.42 | 1709.6209 | 10.08 | 13.2009 | 13.2009 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18385.63 | 1697.23 | 1696.03 | 1709.5897 | 10.47 | 13.5597 | 13.5597 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18405.64 | 1696.9 | 1695.7 | 1709.5586 | 10.8 | 13.8586 | 13.8586 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18425.64 | 1696.9 | 1695.7 | 1709.5274 | 10.8 | 13.8274 | 13.8274 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18445.64 | 1696.89 | 1695.69 | 1709.4963 | 10.81 | 13.8063 | 13.8063 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18465.64 | 1697.23 | 1696.03 | 1709.4651 | 10.47 | 13.4351 | 13.4351 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18485.64 | 1697.19 | 1695.99 | 1709.434 | 10.51 | 13.444 | 13.444 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18505.64 | 1697.05 | 1695.85 | 1709.4028 | 10.65 | 13.5528 | 13.5528 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18525.65 | 1696.46 | 1695.26 | 1709.3716 | 11.24 | 14.1116 | 14.1116 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18545.65 | 1696.28 | 1695.08 | 1709.3405 | 11.42 | 14.2605 | 14.2605 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18565.65 | 1696.05 | 1694.85 | 1709.3093 | 11.65 | 14.4593 | 14.4593 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18585.66 | 1695.68 | 1694.48 | 1709.2782 | 12.02 | 14.7982 | 14.7982 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18605.69 | 1696.85 | 1695.65 | 1709.247 | 10.85 | 13.597 | 13.597 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18625.7 | 1696.35 | 1695.15 | 1709.2158 | 11.35 | 14.0658 | 14.0658 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18645.74 | 1694.95 | 1693.75 | 1709.1846 | 12.75 | 15.4346 | 15.4346 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18665.74 | 1695.04 | 1693.84 | 1709.1534 | 12.66 | 15.3134 | 15.3134 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18685.75 | 1695.22 | 1694.02 | 1709.1222 | 12.48 | 15.1022 | 15.1022 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18705.76 | 1694.46 | 1693.26 | 1709.0911 | 13.24 | 15.8311 | 15.8311 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18725.78 | 1693.54 | 1692.34 | 1709.0599 | 14.16 | 16.7199 | 16.7199 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18745.78 | 1693.54 | 1692.34 | 1709.0287 | 14.16 | 16.6887 | 16.6887 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18765.78 | 1693.63 | 1692.43 | 1708.9976 | 14.07 | 16.5676 | 16.5676 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18785.78 | 1693.63 | 1692.43 | 1708.9664 | 14.07 | 16.5364 | 16.5364 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18805.78 | 1693.37 | 1692.17 | 1708.9353 | 14.33 | 16.7653 | 16.7653 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18825.81 | 1692.36 | 1691.16 | 1708.9041 | 15.34 | 17.7441 | 17.7441 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18845.84 | 1693.42 | 1692.22 | 1708.8729 | 14.28 | 16.6529 | 16.6529 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18865.92 | 1691.64 | 1690.44 | 1708.8416 | 16.06 | 18.4016 | 18.4016 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18885.92 | 1691.56 | 1690.36 | 1708.8105 | 16.14 | 18.4505 | 18.4505 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18905.93 | 1690.92 | 1689.72 | 1708.7793 | 16.78 | 19.0593 | 19.0593 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18925.93 | 1691.1 | 1689.9 | 1708.7481 | 16.6 | 18.8481 | 18.8481 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18945.93 | 1690.99 | 1689.79 | 1708.717 | 16.71 | 18.927 | 18.927 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18965.93 | 1691.09 | 1689.89 | 1708.6858 | 16.61 | 18.7958 | 18.7958 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 18985.93 | 1690.63 | 1689.43 | 1708.6547 | 17.07 | 19.2247 | 19.2247 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19005.93 | 1690.74 | 1689.54 | 1708.6235 | 16.96 | 19.0835 | 19.0835 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19025.93 | 1690.65 | 1689.45 | 1708.5924 | 17.05 | 19.1424 | 19.1424 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19045.93 | 1690.91 | 1689.71 | 1708.5612 | 16.79 | 18.8512 | 18.8512 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19065.94 | 1690.39 | 1689.19 | 1708.53 | 17.31 | 19.34 | 19.34 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19085.95 | 1690.95 | 1689.75 | 1708.4989 | 16.75 | 18.7489 | 18.7489 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19105.95 | 1690.95 | 1689.75 | 1708.4677 | 16.75 | 18.7177 | 18.7177 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19126 | 1691.56 | 1690.36 | 1708.4365 | 16.14 | 18.0765 | 18.0765 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19146 | 1691.82 | 1690.62 | 1708.4053 | 15.88 | 17.7853 | 17.7853 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19166 | 1692.15 | 1690.95 | 1708.3742 | 15.55 | 17.4242 | 17.4242 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19186 | 1692.33 | 1691.13 | 1708.343 | 15.37 | 17.213 | 17.213 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19206.01 | 1692.73 | 1691.53 | 1708.3119 | 14.97 | 16.7819 | 16.7819 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19226.01 | 1692.79 | 1691.59 | 1708.2807 | 14.91 | 16.6907 | 16.6907 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19246.05 | 1694.08 | 1692.88 | 1708.2495 | 13.62 | 15.3695 | 15.3695 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19266.1 | 1694.19 | 1692.99 | 1708.2183 | 13.51 | 15.2283 | 15.2283 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19286.11 | 1694.71 | 1693.51 | 1708.1871 | 12.99 | 14.6771 | 14.6771 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19306.13 | 1695.68 | 1694.48 | 1708.1559 | 12.02 | 13.6759 | 13.6759 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19326.14 | 1696.14 | 1694.94 | 1708.1247 | 11.56 | 13.1847 | 13.1847 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19346.15 | 1696.89 | 1695.69 | 1708.0936 | 10.81 | 12.4036 | 12.4036 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19366.5 | 1697.06 | 1695.86 | 1708.0619 | 10.64 | 12.2019 | 12.2019 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19386.51 | 1697.59 | 1696.39 | 1708.0307 | 10.11 | 11.6407 | 11.6407 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19406.51 | 1697.77 | 1696.57 | 1707.9995 | 9.93 | 11.4295 | 11.4295 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19426.54 | 1698.1 | 1696.9 | 1707.9683 | 9.6 | 11.0683 | 11.0683 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19446.54 | 1698.29 | 1697.09 | 1707.9372 | 9.41 | 10.8472 | 10.8472 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19466.82 | 1698.63 | 1697.43 | 1707.9056 | 9.07 | 10.4756 | 10.4756 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19486.82 | 1698.67 | 1697.47 | 1707.8744 | 9.03 | 10.4044 | 10.4044 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19506.82 | 1698.67 | 1697.47 | 1707.8433 | 9.03 | 10.3733 | 10.3733 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19526.83 | 1698.9 | 1697.7 | 1707.8121 | 8.8 | 10.1121 | 10.1121 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19546.7 | 1699.07 | 1697.87 | 1707.7812 | 8.63 | 9.9112 | 9.9112 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19566.71 | 1698.36 | 1697.16 | 1707.75 | 9.34 | 10.59 | 10.59 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_1 | 19581.43 | 1698.34 | 1697.14 | 1707.7271 | 9.36 | 10.5871 | 10.5871 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_2 | 0 | 1698.34 | 1697.14 | 1707.7271 | 9.36 | 10.5871 | 10.5871 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_2 | 20.02 | 1699.18 | 1697.98 | 1707.697 | 8.52 | 9.717 | 9.717 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_2 | 40.02 | 1699.25 | 1698.05 | 1707.6669 | 8.45 | 9.6169 | 9.6169 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_3 | 0 | 1699.25 | 1698.05 | 1707.6669 | 8.45 | 9.6169 | 9.6169 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_3 | 20 | 1699.6 | 1698.4 | 1707.6411 | 8.1 | 9.2411 | 9.2411 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_3 | 40.27 | 1699.43 | 1698.23 | 1707.6149 | 8.27 | 9.3849 | 9.3849 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_3 | 60.27 | 1699.43 | 1698.23 | 1707.5891 | 8.27 | 9.3591 | 9.3591 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_3 | 80.25 | 1699.49 | 1698.29 | 1707.5632 | 8.21 | 9.2732 | 9.2732 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | BPS_RM_3 | 100.25 | 1699.34 | 1698.14 | 1707.5374 | 8.36 | 9.3974 | 9.3974 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | UHURU_INLET | 0 | 1699.34 | 1698.14 | 1707.5375 | 8.36 | 9.3975 | 9.3975 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | UHURU_INLET | 50 | 1697.3 | 1696.1 | 1707.4769 | 10.4 | 11.3769 | 11.3769 | PN10 | end at tank | no
Z6 Nkangamo-Uhuru | ESR_BRANCH | 0 | 1698.34 | 1697.14 | 1707.7271 | 9.36 | 10.5871 | 10.5871 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | ESR_BRANCH | 38 | 1700 | 1698.8 | 1707.5 | 7.7 | 8.7 | 8.7 | PN10 | end at tank | no
Z6 Nkangamo-Uhuru | GSR01_BRANCH | 0 | 1699.25 | 1698.05 | 1707.6669 | 8.45 | 9.6169 | 9.6169 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | GSR01_BRANCH | 40 | 1698.4 | 1697.2 | 1707.2014 | 9.3 | 10.0014 | 10.0014 | PN10 | end at tank | no
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 0 | 1699.34 | 1698.14 | 1707.5375 | 8.36 | 9.3975 | 9.3975 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 104.99 | 1699.5 | 1698.3 | 1707.3112 | 8.2 | 9.0112 | 9.0112 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 124.99 | 1699.39 | 1698.19 | 1707.2681 | 8.31 | 9.0781 | 9.0781 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 144.99 | 1699.45 | 1698.25 | 1707.225 | 8.25 | 8.975 | 8.975 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 164.99 | 1699.32 | 1698.12 | 1707.1819 | 8.38 | 9.0619 | 9.0619 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 296.09 | 1693.93 | 1692.73 | 1706.8993 | 13.77 | 14.1693 | 14.1693 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 377.83 | 1685.01 | 1683.81 | 1706.7232 | 22.69 | 22.9132 | 22.9132 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 424.97 | 1680.09 | 1678.89 | 1706.6216 | 27.61 | 27.7316 | 27.7316 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 475.02 | 1682.41 | 1681.21 | 1706.5137 | 25.29 | 25.3037 | 25.3037 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 525.03 | 1681.73 | 1680.53 | 1706.406 | 25.97 | 25.876 | 25.97 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 569.16 | 1679.04 | 1677.84 | 1706.3109 | 28.66 | 28.4709 | 28.66 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 619.25 | 1675.96 | 1674.76 | 1706.2029 | 31.74 | 31.4429 | 31.74 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 669.3 | 1673.81 | 1672.61 | 1706.095 | 33.89 | 33.485 | 33.89 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 719.31 | 1672.73 | 1671.53 | 1705.9873 | 34.97 | 34.4573 | 34.97 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 769.33 | 1671.5 | 1670.3 | 1705.8795 | 36.2 | 35.5795 | 36.2 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 819.34 | 1670.35 | 1669.15 | 1705.7717 | 37.35 | 36.6217 | 37.35 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 869.35 | 1669.35 | 1668.15 | 1705.6639 | 38.35 | 37.5139 | 38.35 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 919.35 | 1669.23 | 1668.03 | 1705.5562 | 38.47 | 37.5262 | 38.47 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 969.35 | 1669.51 | 1668.31 | 1705.4484 | 38.19 | 37.1384 | 38.19 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1019.35 | 1669.95 | 1668.75 | 1705.3406 | 37.75 | 36.5906 | 37.75 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1069.35 | 1669.65 | 1668.45 | 1705.2329 | 38.05 | 36.7829 | 38.05 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1119.35 | 1669.8 | 1668.6 | 1705.1251 | 37.9 | 36.5251 | 37.9 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1169.35 | 1669.49 | 1668.29 | 1705.0174 | 38.21 | 36.7274 | 38.21 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1219.36 | 1668.84 | 1667.64 | 1704.9096 | 38.86 | 37.2696 | 38.86 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1269.36 | 1668.49 | 1667.29 | 1704.8018 | 39.21 | 37.5118 | 39.21 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1319.36 | 1668.45 | 1667.25 | 1704.6941 | 39.25 | 37.4441 | 39.25 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1369.36 | 1668.8 | 1667.6 | 1704.5863 | 38.9 | 36.9863 | 38.9 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1419.36 | 1669.31 | 1668.11 | 1704.4786 | 38.39 | 36.3686 | 38.39 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1469.36 | 1669.11 | 1667.91 | 1704.3708 | 38.59 | 36.4608 | 38.59 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1519.37 | 1669.87 | 1668.67 | 1704.263 | 37.83 | 35.593 | 37.83 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1569.37 | 1669.3 | 1668.1 | 1704.1553 | 38.4 | 36.0553 | 38.4 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1612.23 | 1670.03 | 1668.83 | 1704.0629 | 37.67 | 35.2329 | 37.67 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1662.23 | 1670.53 | 1669.33 | 1703.9552 | 37.17 | 34.6252 | 37.17 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1712.24 | 1669.77 | 1668.57 | 1703.8474 | 37.93 | 35.2774 | 37.93 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1753.71 | 1667.42 | 1666.22 | 1703.758 | 40.28 | 37.538 | 40.28 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1803.72 | 1666.8 | 1665.6 | 1703.6502 | 40.9 | 38.0502 | 40.9 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1853.66 | 1665.74 | 1664.54 | 1703.5426 | 41.96 | 39.0026 | 41.96 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1903.67 | 1664.9 | 1663.7 | 1703.4348 | 42.8 | 39.7348 | 42.8 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 1953.73 | 1662.33 | 1661.13 | 1703.327 | 45.37 | 42.197 | 45.37 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2003.88 | 1658.49 | 1657.29 | 1703.2189 | 49.21 | 45.9289 | 49.21 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2054.14 | 1654.27 | 1653.07 | 1703.1106 | 53.43 | 50.0406 | 53.43 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2102.01 | 1651.9 | 1650.7 | 1703.0074 | 55.8 | 52.3074 | 55.8 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2146.65 | 1648.95 | 1647.75 | 1702.9112 | 58.75 | 55.1612 | 58.75 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2196.74 | 1645.98 | 1644.78 | 1702.8032 | 61.72 | 58.0232 | 61.72 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2245.55 | 1642.84 | 1641.64 | 1702.6981 | 64.86 | 61.0581 | 64.86 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2284.56 | 1639.88 | 1638.68 | 1702.614 | 67.82 | 63.934 | 67.82 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2334.62 | 1637.6 | 1636.4 | 1702.5061 | 70.1 | 66.1061 | 70.1 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2383.84 | 1632.79 | 1631.59 | 1702.4 | 74.91 | 70.81 | 74.91 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2434.05 | 1629.07 | 1627.87 | 1702.2918 | 78.63 | 74.4218 | 78.63 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2484.14 | 1626.04 | 1624.84 | 1702.1839 | 81.66 | 77.3439 | 81.66 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2534.24 | 1622.91 | 1621.71 | 1702.0759 | 84.79 | 80.3659 | 84.79 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2584.56 | 1617.27 | 1616.07 | 1701.9674 | 90.43 | 85.8974 | 90.43 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2634.69 | 1613.55 | 1612.35 | 1701.8594 | 94.15 | 89.5094 | 94.15 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2684.95 | 1608.53 | 1607.33 | 1701.7511 | 99.17 | 94.4211 | 99.17 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2734.2 | 1605.94 | 1604.74 | 1701.645 | 101.76 | 96.905 | 101.76 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2776.26 | 1605.36 | 1604.16 | 1701.5543 | 102.34 | 97.3943 | 102.34 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2820.55 | 1604.81 | 1603.61 | 1701.4589 | 102.89 | 97.8489 | 102.89 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2870.57 | 1606.17 | 1604.97 | 1701.3511 | 101.53 | 96.3811 | 101.53 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2918.7 | 1606.52 | 1605.32 | 1701.2473 | 101.18 | 95.9273 | 101.18 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 2968.7 | 1606.54 | 1605.34 | 1701.1396 | 101.16 | 95.7996 | 101.16 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3018.7 | 1606.96 | 1605.76 | 1701.0318 | 100.74 | 95.2718 | 100.74 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3068.76 | 1609.35 | 1608.15 | 1700.9239 | 98.35 | 92.7739 | 98.35 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3118.24 | 1610.13 | 1608.93 | 1700.8173 | 97.57 | 91.8873 | 97.57 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3168.43 | 1611.18 | 1609.98 | 1700.7091 | 96.52 | 90.7291 | 96.52 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3218.43 | 1611.45 | 1610.25 | 1700.6014 | 96.25 | 90.3514 | 96.25 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3267.65 | 1607.28 | 1606.08 | 1700.4953 | 100.42 | 94.4153 | 100.42 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3317.79 | 1603.64 | 1602.44 | 1700.3873 | 104.06 | 97.9473 | 104.06 | PN16 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3365.71 | 1606.93 | 1605.73 | 1700.284 | 100.77 | 94.554 | 100.77 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3415.85 | 1610.66 | 1609.46 | 1700.1759 | 97.04 | 90.7159 | 97.04 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3466.25 | 1613.69 | 1612.49 | 1700.0673 | 94.01 | 87.5773 | 94.01 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3516.25 | 1613.59 | 1612.39 | 1699.9596 | 94.11 | 87.5696 | 94.11 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3566.25 | 1613.36 | 1612.16 | 1699.8518 | 94.34 | 87.6918 | 94.34 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3613.63 | 1612.62 | 1611.42 | 1699.7497 | 95.08 | 88.3297 | 95.08 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3656.26 | 1618.81 | 1617.61 | 1699.6578 | 88.89 | 82.0478 | 88.89 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3703.37 | 1625.04 | 1623.84 | 1699.5563 | 82.66 | 75.7163 | 82.66 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3742.55 | 1628.49 | 1627.29 | 1699.4719 | 79.21 | 72.1819 | 79.21 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3792.59 | 1634.14 | 1632.94 | 1699.364 | 73.56 | 66.424 | 73.56 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3842.83 | 1636.75 | 1635.55 | 1699.2557 | 70.95 | 63.7057 | 70.95 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3879.56 | 1640.56 | 1639.36 | 1699.1766 | 67.14 | 59.8166 | 67.14 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3929.46 | 1645.45 | 1644.25 | 1699.069 | 62.25 | 54.819 | 62.25 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 3978.69 | 1652.18 | 1650.98 | 1698.963 | 55.52 | 47.983 | 55.52 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 4024.59 | 1657.81 | 1656.61 | 1698.864 | 49.89 | 42.254 | 49.89 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 4075.79 | 1668.81 | 1667.61 | 1698.7537 | 38.89 | 31.1437 | 38.89 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 4126.78 | 1676.83 | 1675.63 | 1698.6438 | 30.87 | 23.0138 | 30.87 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 4169.11 | 1679.38 | 1678.18 | 1698.5526 | 28.32 | 20.3726 | 28.32 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 4217.54 | 1684.62 | 1683.42 | 1698.4482 | 23.08 | 15.0282 | 23.08 | PN10 | OK | yes
Z6 Nkangamo-Uhuru | IPITO_BRANCH | 4220.82 | 1684.57 | 1683.37 | 1698.4411 | 23.13 | 15.0711 | 23.13 | PN10 | end at tank | no
Z7 Uhuru-Chapwa | UHURU_J004N | 0 | 1699.34 | 1698.14 | 1697.6 | 4.16 | -0.54 | 4.16 | PN10 | end at tank | no
Z7 Uhuru-Chapwa | UHURU_J004N | 97.19 | 1699.05 | 1697.85 | 1696.9564 | 4.45 | -0.8936 | 4.45 | PN10 | NEGATIVE | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 139.33 | 1698.85 | 1697.65 | 1696.6774 | 4.65 | -0.97265 | 4.65 | PN10 | NEGATIVE | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 159.33 | 1699.12 | 1697.92 | 1696.5449 | 4.38 | -1.3751 | 4.38 | PN10 | NEGATIVE | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 179.34 | 1699.52 | 1698.32 | 1696.4124 | 3.98 | -1.9076 | 3.98 | PN10 | NEGATIVE | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 252.76 | 1697.64 | 1696.44 | 1695.9262 | 5.86 | -0.51379 | 5.86 | PN10 | NEGATIVE | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 367.16 | 1691.16 | 1689.96 | 1695.1687 | 12.34 | 5.2087 | 12.34 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 416.63 | 1688.29 | 1687.09 | 1694.8411 | 15.21 | 7.7511 | 15.21 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 466.72 | 1685.26 | 1684.06 | 1694.5094 | 18.24 | 10.4494 | 18.24 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 516.78 | 1682.85 | 1681.65 | 1694.1779 | 20.65 | 12.5279 | 20.65 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 566.37 | 1679.71 | 1678.51 | 1693.8495 | 23.79 | 15.3395 | 23.79 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 616.45 | 1676.76 | 1675.56 | 1693.5178 | 26.74 | 17.9578 | 26.74 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 666.25 | 1674.36 | 1673.16 | 1693.1881 | 29.14 | 20.0281 | 29.14 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 716.37 | 1670.92 | 1669.72 | 1692.8562 | 32.58 | 23.1362 | 32.58 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 765.46 | 1668.95 | 1667.75 | 1692.5311 | 34.55 | 24.7811 | 34.55 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 815.3 | 1665.91 | 1664.71 | 1692.2011 | 37.59 | 27.4911 | 37.59 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 865 | 1663.08 | 1661.88 | 1691.8719 | 40.42 | 29.9919 | 40.42 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 915.09 | 1660.12 | 1658.92 | 1691.5402 | 43.38 | 32.6202 | 43.38 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 964.33 | 1656.85 | 1655.65 | 1691.2142 | 46.65 | 35.5642 | 46.65 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1014.44 | 1653.52 | 1652.32 | 1690.8823 | 49.98 | 38.5623 | 49.98 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1064.64 | 1650.16 | 1648.96 | 1690.5499 | 53.34 | 41.5899 | 53.34 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1114.74 | 1646.97 | 1645.77 | 1690.2181 | 56.53 | 44.4481 | 56.53 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1165.13 | 1644.55 | 1643.35 | 1689.8845 | 58.95 | 46.5345 | 58.95 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1215.41 | 1641.32 | 1640.12 | 1689.5515 | 62.18 | 49.4315 | 62.18 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1265.59 | 1639.86 | 1638.66 | 1689.2192 | 63.64 | 50.5592 | 63.64 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1315.31 | 1637.92 | 1636.72 | 1688.89 | 65.58 | 52.17 | 65.58 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1365.32 | 1636.53 | 1635.33 | 1688.5588 | 66.97 | 53.2288 | 66.97 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1415.09 | 1635.37 | 1634.17 | 1688.2292 | 68.13 | 54.0592 | 68.13 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1464.04 | 1634.52 | 1633.32 | 1687.9051 | 68.98 | 54.5851 | 68.98 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1514.49 | 1633.93 | 1632.73 | 1687.571 | 69.57 | 54.841 | 69.57 | PN10 | OK | yes
Z7 Uhuru-Chapwa | UHURU_J004N | 1563.45 | 1630.08 | 1628.88 | 1687.2468 | 73.42 | 58.3668 | 73.42 | PN10 | OK | yes
Z7 Uhuru-Chapwa | MAKAMBINI_BRANCH | 0 | 1630.08 | 1628.88 | 1687.2464 | 73.42 | 58.3664 | 73.42 | PN10 | OK | yes
Z7 Uhuru-Chapwa | MAKAMBINI_BRANCH | 494 | 1655.7 | 1654.5 | 1680.7175 | 47.8 | 26.2175 | 47.8 | PN10 | end at tank | no
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 0 | 1630.08 | 1628.88 | 1687.2464 | 73.42 | 58.3664 | 73.42 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 50.01 | 1628.93 | 1627.73 | 1686.5855 | 74.57 | 58.8555 | 74.57 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 99.84 | 1627.22 | 1626.02 | 1685.9269 | 76.28 | 59.9069 | 76.28 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 149.86 | 1626.03 | 1624.83 | 1685.2658 | 77.47 | 60.4358 | 77.47 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 199.89 | 1626.06 | 1624.86 | 1684.6046 | 77.44 | 59.7446 | 77.44 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 250.23 | 1625.26 | 1624.06 | 1683.9393 | 78.24 | 59.8793 | 78.24 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 300.54 | 1621.68 | 1620.48 | 1683.2743 | 81.82 | 62.7943 | 81.82 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 350.54 | 1619.86 | 1618.66 | 1682.6135 | 83.64 | 63.9535 | 83.64 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 400.8 | 1616.72 | 1615.52 | 1681.9492 | 86.78 | 66.4292 | 86.78 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 451.07 | 1613.61 | 1612.41 | 1681.2848 | 89.89 | 68.8748 | 89.89 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 501.19 | 1610.18 | 1608.98 | 1680.6224 | 93.32 | 71.6424 | 93.32 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 550.84 | 1606.37 | 1605.17 | 1679.9662 | 97.13 | 74.7962 | 97.13 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 599.18 | 1602.64 | 1601.44 | 1679.3273 | 100.86 | 77.8873 | 100.86 | PN10 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 646.43 | 1599.82 | 1598.62 | 1678.7028 | 103.68 | 80.0828 | 103.68 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 696.82 | 1595.87 | 1594.67 | 1678.0369 | 107.63 | 83.3669 | 107.63 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 746.46 | 1592.46 | 1591.26 | 1677.3808 | 111.04 | 86.1208 | 111.04 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 795.94 | 1590.45 | 1589.25 | 1676.7268 | 113.05 | 87.4768 | 113.05 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 845.96 | 1586.91 | 1585.71 | 1676.0657 | 116.59 | 90.3557 | 116.59 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 895.93 | 1584.03 | 1582.83 | 1675.4053 | 119.47 | 92.5753 | 119.47 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 946 | 1581.45 | 1580.25 | 1674.7436 | 122.05 | 94.4936 | 122.05 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 994.92 | 1578.02 | 1576.82 | 1674.097 | 125.48 | 97.277 | 125.48 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1044.57 | 1575.98 | 1574.78 | 1673.4408 | 127.52 | 98.6608 | 127.52 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1093.79 | 1571.53 | 1570.33 | 1672.7903 | 131.97 | 102.4603 | 131.97 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1143.99 | 1568.19 | 1566.99 | 1672.1268 | 135.31 | 105.1368 | 135.31 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1193.67 | 1565.59 | 1564.39 | 1671.4702 | 137.91 | 107.0802 | 137.91 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1243.61 | 1564.62 | 1563.42 | 1670.8102 | 138.88 | 107.3902 | 138.88 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1293.64 | 1563.07 | 1561.87 | 1670.1489 | 140.43 | 108.2789 | 140.43 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1343.66 | 1562.57 | 1561.37 | 1669.4879 | 140.93 | 108.1179 | 140.93 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1393.66 | 1562.56 | 1561.36 | 1668.827 | 140.94 | 107.467 | 140.94 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1443.7 | 1561.98 | 1560.78 | 1668.1657 | 141.52 | 107.3857 | 141.52 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1493.71 | 1562.95 | 1561.75 | 1667.5047 | 140.55 | 105.7547 | 140.55 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1542.68 | 1562.88 | 1561.68 | 1666.8575 | 140.62 | 105.1775 | 140.62 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1593.05 | 1563.49 | 1562.29 | 1666.1918 | 140.01 | 103.9018 | 140.01 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1643.07 | 1562.15 | 1560.95 | 1665.5307 | 141.35 | 104.5807 | 141.35 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1693.14 | 1561.43 | 1560.23 | 1664.8689 | 142.07 | 104.6389 | 142.07 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1743.15 | 1562.33 | 1561.13 | 1664.208 | 141.17 | 103.078 | 141.17 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1792.17 | 1563.91 | 1562.71 | 1663.5601 | 139.59 | 100.8501 | 139.59 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1841.45 | 1564.17 | 1562.97 | 1662.9088 | 139.33 | 99.9388 | 139.33 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1891.2 | 1562.44 | 1561.24 | 1662.2512 | 141.06 | 101.0112 | 141.06 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1941.32 | 1560.75 | 1559.55 | 1661.5888 | 142.75 | 102.0388 | 142.75 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 1991.39 | 1558.07 | 1556.87 | 1660.9271 | 145.43 | 104.0571 | 145.43 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2041.61 | 1553.44 | 1552.24 | 1660.2633 | 150.06 | 108.0233 | 150.06 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2090.78 | 1552.39 | 1551.19 | 1659.6135 | 151.11 | 108.4235 | 151.11 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2139.77 | 1553.2 | 1552 | 1658.966 | 150.3 | 106.966 | 150.3 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2189.78 | 1554.04 | 1552.84 | 1658.305 | 149.46 | 105.465 | 149.46 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2240.02 | 1558.94 | 1557.74 | 1657.641 | 144.56 | 99.901 | 144.56 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2290.05 | 1560.76 | 1559.56 | 1656.9798 | 142.74 | 97.4198 | 142.74 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2340.06 | 1560.21 | 1559.01 | 1656.3189 | 143.29 | 97.3089 | 143.29 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2389.69 | 1557.67 | 1556.47 | 1655.6629 | 145.83 | 99.1929 | 145.83 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2439.8 | 1554.32 | 1553.12 | 1655.0006 | 149.18 | 101.8806 | 149.18 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2489.66 | 1552.01 | 1550.81 | 1654.3417 | 151.49 | 103.5317 | 151.49 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2538.5 | 1546.35 | 1545.15 | 1653.6962 | 157.15 | 108.5462 | 157.15 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2586.9 | 1542.67 | 1541.47 | 1653.0565 | 160.83 | 111.5865 | 160.83 | PN16 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2637.44 | 1536.03 | 1534.83 | 1652.3885 | 167.47 | 117.5585 | 167.47 | PN25 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2687.71 | 1530.88 | 1529.68 | 1651.7241 | 172.62 | 122.0441 | 172.62 | PN25 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2737.56 | 1525.37 | 1524.17 | 1651.0653 | 178.13 | 126.8953 | 178.13 | PN25 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2781.84 | 1523.93 | 1522.73 | 1650.48 | 179.57 | 127.75 | 179.57 | PN25 | OK | yes
Z7 Uhuru-Chapwa | CHAPWA_BRANCH | 2790.5 | 1523.81 | 1522.61 | 1650.3656 | 179.69 | 127.7556 | 179.69 | PN25 | end at tank | no